SITE SURVEY REPORT & ASSESSMENT DATA
Rooftop Solar Power Plant

### 1. SITE INFORMATION

| Parameter | Details |
| --- | --- |
| Survey Date | [Insert Date] |
| Site Location | [Insert Address] |
| GPS Coordinates | [Latitude, Longitude] |
| Altitude | [in meters] |
| Contact Person | [Name & Contact Info] |
| Site Type | RCC Flat Roof / Industrial Shed / etc. |
| Grid Availability | Yes / No |
| Net Metering Allowed | Yes / No |

### 2. SOLAR RESOURCE ASSESSMENT

| Parameter | Value |
| --- | --- |
| Average Irradiance | [e.g., 5.2 kWh/m²/day] |
| Solar Window | [e.g., 9 AM to 4 PM] |
| Data Source | [e.g., PVGIS, NASA, MNRE] |
| Suggested Tilt Angle | = Latitude of Location |

Formula: Estimated Annual Generation (kWh/year) = Installed Capacity (kW) × Avg. Irradiance × 365 × PR
Where PR (Performance Ratio) is typically 0.75 to 0.85

### 3. ROOF ANALYSIS

| Parameter | Value |
| --- | --- |
| Total Rooftop Area | [in m²] |
| Usable Area (80%) | = Total Area × 0.8 |
| Area per kW (Mono PERC) | ~6.5 m²/kW |
| Max System Capacity | = Usable Area ÷ 6.5 |

### 4. LOAD ANALYSIS

| Parameter | Value |
| --- | --- |
| Monthly Consumption | [kWh] |
| Daily Load | = Monthly ÷ 30 |
| Suggested Capacity | = Daily Load ÷ Irradiance |

### 5. SYSTEM SIZING SUMMARY

| Parameter | Value |
| --- | --- |
| Proposed Capacity | [in kWp] |
| Module Rating | [e.g., 540 Wp] |
| Number of Modules | = Proposed × 1000 ÷ Rating |
| Inverter Capacity | ~ 90-100% of DC size |
| Required Area | = Proposed × 6.5 m² |

### 6. SHADING / OBSTRUCTION ASSESSMENT

| Obstruction Location | Description |
| --- | --- |
| North | [e.g., HVAC Units] |
| East | [e.g., Parapet Wall] |
| South | [Open] |
| West | [Water Tank] |
| Method Used | Sun Path Diagram / Visual / Solmetric SunEye |

### 7. STRUCTURAL EVALUATION

| Parameter | Value |
| --- | --- |
| Roof Type | RCC / Metal / Other |
| Load Capacity | [kg/m²] |
| Weight of PV Structure | ~20 kg/m² |
| Suitability | [Suitable / Not Suitable] |

### 8. EXAMPLE CALCULATION:

Given:

- Daily Load = 400 kWh/day

- Avg Irradiance = 5.2 kWh/m²/day

- PR = 0.75

Required Capacity = 400 / (5.2 × 0.75) ≈ 102.5 kW

Available Roof = 640 m²
Max Capacity = 640 / 6.5 ≈ 98.5 kW

System is feasible with minimal adjustment

### 9. CONCLUSION

- Recommended System: [e.g., 80 kWp Mono PERC]

- Roof area is sufficient

- Grid availability confirmed

- Net metering applicable

- Shading impact is minimal

- Structural strength adequate

Prepared By: [Your Company Name]
Contact: contact@flasysdesign.com | +91 7011558555