## DC Voltage Drop
DC VOLTAGE DROP CALCULATION
Project name: |  | 400.4kWp
Client Name:
Voltage: |  |  |  | Resistance: |  | 0.00461 | Ohm/km
Ambient Temperature: |  |  |  | Current: |  | 9.55 | Ampere
Grouping Factor:
| Voltage Drop (Vd): |  | = | (2 x L x I x R)/1000
| %Voltage Drop: |  | = | (Vd/Source Voltage) x 100
SR. NO. | String | Module to inverter NO: |  | DC Cable Length (Meter) |  | Total Length | Power Loss W (IxIxRxL) | %Voltage Drop
|  |  |  | Positive | Negative
1 | String 1 | INVERTER 1 |  | 11 | 14 | 25 | 10.5111 | 0.30337
2 | String 2 |  |  | 4 | 6 | 10 | 4.2044 | 0.12135
3 | String 3 |  |  | 4 | 6 | 10 | 4.2044 | 0.12135
4 | String 4 |  |  | 12 | 14 | 26 | 10.9315 | 0.31551
| TOTAL LENGTH: |  |  |  |  | 71
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.31551
1 | String 1 | INVERTER 2 |  | 12 | 14 | 26 | 10.9315 | 0.31551
2 | String 2 |  |  | 5 | 6 | 11 | 4.6249 | 0.13348
3 | String 3 |  |  | 4 | 7 | 11 | 4.6249 | 0.13348
4 | String 4 |  |  | 14 | 15 | 29 | 12.1929 | 0.35191
TOTAL LENGTH:
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.35191
1 | String 1 | INVERTER 3 |  | 5 | 7 | 12 | 5.0453 | 0.14562
2 | String 2 |  |  | 5 | 6 | 11 | 4.6249 | 0.13348
3 | String 3 |  |  | 16 | 15 | 31 | 13.0337 | 0.37618
4 | String 4 |  |  | 14 | 14 | 28 | 11.7724 | 0.33978
TOTAL LENGTH:
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.37618
1 | String 1 | INVERTER 4 |  | 11 | 9 | 20 | 8.4089 | 0.2427
2 | String 2 |  |  | 11 | 9 | 20 | 8.4089 | 0.2427
3 | String 3 |  |  | 6 | 7 | 13 | 5.4658 | 0.15775
4 | String 4 |  |  | 5 | 6 | 11 | 4.6249 | 0.13348
TOTAL LENGTH:
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.2427
1 | String 1 | INVERTER 5 |  | 10 | 7 | 17 | 7.1475 | 0.20629
2 | String 2 |  |  | 4 | 6 | 10 | 4.2044 | 0.12135
3 | String 3 |  |  | 4 | 6 | 10 | 4.2044 | 0.12135
4 | String 4 |  |  | 12 | 14 | 26 | 10.9315 | 0.31551
TOTAL LENGTH:
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.31551

## AC Voltage Drop
AC VOLTAGE DROP CALCULATION
Project name: |  | 400.4kWp
Client Name:
Inverter Specifications:
| Rated kVA |  |  | : | 20
| Rated Voltage (V): |  |  | : | 415
| Rated Current (IL): |  |  | : | 15
Cable Parameter (As per Polycab):
Derating factors:
Cable Laid in Ground
| Temperature Correction |  |  | : | 0.8 | (50°C Ground Temperature)
| Grouping |  |  | : | 1
| Total Derating |  |  | : | 0.8
Continous current of Selected Cable
| Type |  | Size |  | Current Rating in Ground (Ampere) | Derated Current (Ampere)
| 4C, Cu, FRLS Cable |  | 16 Sqmm |  | 95 | 76
Verification of cable sizing according to permissible voltage drop
| Voltage Drop %V (3ϕ): |  |  | = | {√3*IL*L*(R Cosϕ+ X Sinϕ)}*100/(N*V)
| R | = | Conductor Resistace
| X | = | Conductor Reactance
| L | = | Cable Length in KM (kilometer)
| N | = | Number of Runs
| Cos(ϕ) | = | Power Factor |  |  | (Power factor is nearly equal to 1)
| Sin(ϕ) | = | Component of Reactive Power |  |  | (Assumed as Zero)
| IL | = | Rated Current
| V | = | Rated Voltage
SR. NO. | FROM INVERTER No: | TO ACCB No: |  | Resistance (R) of Cable (Ohm/Km) | Reactance (X) of Cable (Ohm/Km) | Total Length in (Kilometer) | Number of Run | %Voltage Drop
1 | Inverter 1 | ACCB 1 |  | 1.4 | 0.08 | 0.033 | 1 | 0.28922
2 | Inverter 2 |  |  |  |  | 0.019 | 1 | 0.16652
3 | Inverter 3 |  |  |  |  | 0.029 | 1 | 0.25417
4 | Inverter 4 |  |  |  |  | 0.05 | 1 | 0
4 | Inverter 11 |  |  |  |  | 0.037 | 1 | 0
| TOTAL LENGTH: |  |  |  |  | 0.168
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.28922
1 | Inverter 5 | ACCB 2
2 | Inverter 6
3 | Inverter 7
4 | Inverter 8
4 | Inverter 9
TOTAL LENGTH:
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0
1 | Inverter 14 | ACCB 3
2 | Inverter 15
3 | Inverter 16
4 | Inverter 17
4 | Inverter 10
TOTAL LENGTH:
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0
1 | Inverter 12 | ACCB 4
2 | Inverter 13
3 | Inverter 18
4 | Inverter 19
4 | Inverter 20
SR. NO. | FROM ACCB No: | TO MAIN ACCB |  | Cable Type | AC Cable Length (Meter) | Total Length |  | %Voltage Drop
1 | ACCB 1 | MAIN ACCB
2 | ACCB 2
3 | ACCB 3
4 | ACCB 4

## AC Voltage Drop 25kW Inverter
AC VOLTAGE DROP CALCULATION
Project name: |  | 400.4kWp
Client Name:
Inverter Specifications:
| Rated kVA |  |  | : | 25
| Rated Voltage (V): |  |  | : | 415
| Rated Current (IL): |  |  | : | 36.2 | (from Inverter Specsheet)
Cable Parameter (As per Polycab):
Derating factors:
Cable Laid in Ground
| Temperature Correction |  |  | : | 0.8 | (50°C Ground Temperature)
| Grouping |  |  | : | 1
| Total Derating |  |  | : | 0.8
Continous current of Selected Cable
| Type |  | Size |  | Current Rating in Ground (Ampere) | Derated Current (Ampere)
| 4C, Cu, FRLS Cable |  | 16 Sqmm |  | 95 | 76
Verification of cable sizing according to permissible voltage drop
| Voltage Drop %V (3ϕ): |  |  | = | {√3*IL*L*(R Cosϕ+ X Sinϕ)}*100/(N*V)
| R | = | Conductor Resistace
| X | = | Conductor Reactance
| L | = | Cable Length in KM (kilometer)
| N | = | Number of Runs
| Cos(ϕ) | = | Power Factor |  |  | (Power factor is nearly equal to 1)
| Sin(ϕ) | = | Component of Reactive Power |  |  | (Assumed as Zero)
| IL | = | Rated Current
| V | = | Rated Voltage
SR. NO. | FROM INVERTER No: | TO ACCB No: |  | Resistance (R) of Cable (Ohm/Km) | Reactance (X) of Cable (Ohm/Km) | Total Length in (Kilometer) | Number of Run | %Voltage Drop
1 | Inverter 1 | ACCB 1 |  | 1.4 | 0.08 | 0.028 | 1 | 0.59224
2 | Inverter 2 |  |  |  |  | 0.014 | 1 | 0.29612
3 | Inverter 3 |  |  |  |  | 0.03 | 1 | 0.63454
4 | Inverter 9 |  |  |  |  | 0.024 | 1 | 0.50763
| TOTAL LENGTH: |  |  |  |  | 0.096
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.63454
1 | Inverter 4 | ACCB 2 |  | 1.4 | 0.08 | 0.022 | 1 | 0.46533
2 | Inverter 5 |  |  |  |  | 0.008 | 1 | 0.16921
3 | Inverter 6 |  |  |  |  | 0.023 | 1 | 0.48648
4 | Inverter 7 |  |  |  |  | 0.027 | 1 | 0.57108
| TOTAL LENGTH: |  |  |  |  | 0.08
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.57108
1 | Inverter 8 | ACCB 3 |  | 1.4 | 0.08 | 0.029 | 1 | 0.61339
2 | Inverter 12 |  |  |  |  | 0.015 | 1 | 0.31727
3 | Inverter 13 |  |  |  |  | 0.018 | 1 | 0.38072
4 | Inverter 14 |  |  |  |  | 0.024 | 1 | 0.50763
| TOTAL LENGTH: |  |  |  |  | 0.086
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.61339
1 | Inverter 10 | ACCB 4 |  | 1.4 | 0.08 | 0.023 | 1 | 0.48648
2 | Inverter 11 |  |  |  |  | 0.011 | 1 | 0.23266
3 | Inverter 15 |  |  |  |  | 0.019 | 1 | 0.40187
4 | Inverter 16 |  |  |  |  | 0.033 | 1 | 0.69799
| TOTAL LENGTH: |  |  |  |  | 0.086
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.69799
Average Voltage drop from Inverter to ACCB = | [5 empty] | 0.46004 | %
AC VOLTAGE DROP FROM ACCB1, ACCB2, ACCB3 AND ACCB4 TO ACCB5
| Rated Voltage (V): |  |  | : | 415
| Rated Current (IL): |  |  | : | 144.8
Cable Parameter (As per Polycab):
Derating factors:
Cable Laid in Ground
| Temperature Correction |  |  | : | 0.8 | (50°C Ground Temperature)
| Grouping |  |  | : | 1
| Total Derating |  |  | : | 0.8
Continous current of Selected Cable
| Type |  | Size |  | Current Rating in Ground (Ampere) | Derated Current (Ampere)
| 3.5C, Al, FRLS Cable |  | 185 Sqmm |  | 282 | 225.6
SR. NO. | FROM ACCB No: | TO ACCB No: |  | Resistance (R) of Cable (Ohm/Km) | Reactance (X) of Cable (Ohm/Km) | Total Length in (Kilometer) | Number of Run | %Voltage Drop
1 | ACCB 1 | ACCB 5 |  | 0.198 | 0.0895 | 0.013 | 1 | 0.15555
2 | ACCB 2 |  |  |  |  | 0.062 | 1 | 0.74187
3 | ACCB 3 |  |  |  |  | 0.078 | 1 | 0.93331
4 | ACCB 4 |  |  |  |  | 0.06 | 1 | 0.71793
| TOTAL LENGTH: |  |  |  |  | 0.213
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.93331
AC VOLTAGE DROP FROM ACCB5 TO MAIN ACCB
| Rated Voltage (V): |  |  | : | 415
| Rated Current (IL): |  |  | : | 579.2
Cable Parameter (As per Polycab):
Derating factors:
Cable Laid in Ground
| Temperature Correction |  |  | : | 0.9
| Grouping |  |  | : | 1
| Total Derating |  |  | : | 0.9
Continous current of Selected Cable
| Type |  | Size |  | Current Rating in Ground (Ampere) | Derated Current (Ampere)
| 3.5C, Al, FRLS Cable |  | 240 Sqmm |  | 327 | 294.3
SR. NO. | FROM ACCB No: | TO ACCB |  | Resistance (R) of Cable (Ohm/Km) | Reactance (X) of Cable (Ohm/Km) | Total Length in (Kilometer) | Number of Run | %Voltage Drop
1 | ACCB 5 | MAIN ACCB |  | 0.15 | 0.0876 | 0.13 | 2 | 2.3569
| TOTAL LENGTH: |  |  |  |  | 0.13
| MAXIMUM VOLTAGE DROP: | [6 empty] | 2.3569
AC VOLTAGE DROP FROM MAIN ACCB TO TERMINATION POINT
| Rated Voltage (V): |  |  | : | 415
| Rated Current (IL): |  |  | : | 579.2
Cable Parameter (As per Polycab):
Derating factors:
Cable Laid in Ground
| Temperature Correction |  |  | : | 0.9
| Grouping |  |  | : | 1
| Total Derating |  |  | : | 0.9
Continous current of Selected Cable
| Type |  | Size | Current Rating in Ground (Ampere) | Derated Current (Ampere) | Total Current Carrying Capacity of 2 Run Cable
| 3.5C, Al, FRLS Cable |  | 240 Sqmm | 327 | 294.3 | 588.6
SR. NO. | FROM ACCB No: | TO ACCB |  | Resistance (R) of Cable (Ohm/Km) | Reactance (X) of Cable (Ohm/Km) | Total Length in (Kilometer) | Number of Run | %Voltage Drop
1 | MAIN ACCB | TERMINATION POINT |  | 0.15 | 0.0876 | 0.02 | 2 | 0.36259
| TOTAL LENGTH: |  |  |  |  | 0.02
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.36259

## DC Voltage drop 25kW
DC VOLTAGE DROP CALCULATION
Project name: |  | 400.4kWp
Client Name:
Voltage: |  |  | 725.6V | Resistance: |  | 0.00461 | Ohm/km
Ambient Temperature: |  |  | 41.7°C | Current: |  | 9.55 | Ampere
Grouping Factor: |  |  | 1
| Voltage Drop (Vd): |  | = | (2 x L x I x R)/1000
| %Voltage Drop: |  | = | (Vd/Source Voltage) x 100
SR. NO. | String | Module to inverter NO: |  | DC Cable Length (Meter) |  | Total Length | Power Loss W (IxIxRxL) | %Voltage Drop
|  |  |  | Positive | Negative
1 | String 1 | INVERTER 1 |  | 14 | 16 | 30 | 12.6133 | 0.36405
2 | String 2 |  |  | 7 | 8 | 15 | 6.3067 | 0.18202
3 | String 3 |  |  | 7 | 9 | 16 | 6.7271 | 0.19416
4 | String 4 |  |  | 19 | 22 | 41 | 17.2382 | 0.49753
5 | String 5 |  |  | 26 | 29 | 55 | 23.1244 | 0.66742
| TOTAL LENGTH: |  |  |  |  | 157
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.66742
1 | String 1 | INVERTER 2 |  | 22 | 24 | 46 | 19.3404 | 0.55821
2 | String 2 |  |  | 15 | 16 | 31 | 13.0337 | 0.37618
3 | String 3 |  |  | 7 | 8 | 15 | 6.3067 | 0.18202
4 | String 4 |  |  | 7 | 8 | 15 | 6.3067 | 0.18202
5 | String 5 |  |  | 15 | 16 | 31 | 13.0337 | 0.37618
| TOTAL LENGTH: |  |  |  |  | 138
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.55821
1 | String 1 | INVERTER 3 |  | 8 | 10 | 18 | 7.568 | 0.21843
2 | String 2 |  |  | 7 | 9 | 16 | 6.7271 | 0.19416
3 | String 3 |  |  | 12 | 14 | 26 | 10.9315 | 0.31551
4 | String 4 |  |  | 14 | 17 | 31 | 13.0337 | 0.37618
5 | String 5 |  |  | 14 | 17 | 31 | 13.0337 | 0.37618
| TOTAL LENGTH: |  |  |  |  | 122
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.37618
1 | String 1 | INVERTER 4 |  | 12 | 11 | 23 | 9.6702 | 0.2791
2 | String 2 |  |  | 12 | 14 | 26 | 10.9315 | 0.31551
3 | String 3 |  |  | 7 | 11 | 18 | 7.568 | 0.21843
4 | String 4 |  |  | 8 | 11 | 19 | 7.9884 | 0.23056
5 | String 5 |  |  | 18 | 21 | 39 | 16.3973 | 0.47326
| TOTAL LENGTH: |  |  |  |  | 125
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.47326
1 | String 1 | INVERTER 5 |  | 13 | 10 | 23 | 9.6702 | 0.2791
2 | String 2 |  |  | 13 | 11 | 24 | 10.0906 | 0.29124
3 | String 3 |  |  | 12 | 13 | 25 | 10.5111 | 0.30337
4 | String 4 |  |  | 11 | 14 | 25 | 10.5111 | 0.30337
5 | String 5 |  |  | 19 | 21 | 40 | 16.8177 | 0.4854
| TOTAL LENGTH: |  |  |  |  | 137
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.4854
SR. NO. | String | Module to inverter NO: |  | DC Cable Length (Meter) |  | Total Length | Power Loss W (IxIxRxL) | %Voltage Drop
|  |  |  | Positive | Negative
1 | String 1 | INVERTER 6 |  | 17 | 15 | 32 | 13.4542 | 0.38832
2 | String 2 |  |  | 11 | 8 | 19 | 7.9884 | 0.23056
3 | String 3 |  |  | 10 | 9 | 19 | 7.9884 | 0.23056
4 | String 4 |  |  | 7 | 9 | 16 | 6.7271 | 0.19416
5 | String 5 |  |  | 7 | 9 | 16 | 6.7271 | 0.19416
| TOTAL LENGTH: |  |  |  |  | 102
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.38832
1 | String 1 | INVERTER 7 |  | 19 | 20 | 39 | 16.3973 | 0.47326
2 | String 2 |  |  | 12 | 13 | 25 | 10.5111 | 0.30337
3 | String 3 |  |  | 7 | 10 | 17 | 7.1475 | 0.20629
4 | String 4 |  |  | 8 | 10 | 18 | 7.568 | 0.21843
5 | String 5 |  |  | 18 | 20 | 38 | 15.9769 | 0.46113
| TOTAL LENGTH: |  |  |  |  | 137
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.47326
1 | String 1 | INVERTER 8 |  | 13 | 11 | 24 | 10.0906 | 0.29124
2 | String 2 |  |  | 13 | 11 | 24 | 10.0906 | 0.29124
3 | String 3 |  |  | 14 | 16 | 30 | 12.6133 | 0.36405
4 | String 4 |  |  | 6 | 9 | 15 | 6.3067 | 0.18202
5 | String 5 |  |  | 7 | 9 | 16 | 6.7271 | 0.19416
| TOTAL LENGTH: |  |  |  |  | 109
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.36405
1 | String 1 | INVERTER 9 |  | 6 | 9 | 15 | 6.3067 | 0.18202
2 | String 2 |  |  | 6 | 9 | 15 | 6.3067 | 0.18202
3 | String 3 |  |  | 14 | 18 | 32 | 13.4542 | 0.38832
4 | String 4 |  |  | 15 | 17 | 32 | 13.4542 | 0.38832
5 | String 5 |  |  | 22 | 27 | 49 | 20.6017 | 0.59461
| TOTAL LENGTH: |  |  |  |  | 143
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.59461
1 | String 1 | INVERTER 10 |  | 25 | 27 | 52 | 21.8631 | 0.63102
2 | String 2 |  |  | 24 | 27 | 51 | 21.4426 | 0.61888
3 | String 3 |  |  | 7 | 9 | 16 | 6.7271 | 0.19416
4 | String 4 |  |  | 16 | 19 | 35 | 14.7155 | 0.42472
5 | String 5 |  |  | 15 | 18 | 33 | 13.8746 | 0.40045
| TOTAL LENGTH: |  |  |  |  | 187
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.63102
1 | String 1 | INVERTER 11 |  | 8 | 10 | 18 | 7.568 | 0.21843
2 | String 2 |  |  | 8 | 10 | 18 | 7.568 | 0.21843
3 | String 3 |  |  | 18 | 20 | 38 | 15.9769 | 0.46113
4 | String 4 |  |  | 15 | 16 | 31 | 13.0337 | 0.37618
5 | String 5 |  |  | 16 | 17 | 33 | 13.8746 | 0.40045
| TOTAL LENGTH: |  |  |  |  | 138
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.46113
1 | String 1 | INVERTER 12 |  | 11 | 9 | 20 | 8.4089 | 0.2427
2 | String 2 |  |  | 8 | 8 | 16 | 6.7271 | 0.19416
3 | String 3 |  |  | 8 | 10 | 18 | 7.568 | 0.21843
4 | String 4 |  |  | 13 | 16 | 29 | 12.1929 | 0.35191
5 | String 5 |  |  | 13 | 15 | 28 | 11.7724 | 0.33978
| TOTAL LENGTH: |  |  |  |  | 111
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.35191
SR. NO. | String | Module to inverter NO: |  | DC Cable Length (Meter) |  | Total Length | Power Loss W (IxIxRxL) | %Voltage Drop
|  |  |  | Positive | Negative
1 | String 1 | INVERTER 13 |  | 13 | 20 | 33 | 13.8746 | 0.40045
2 | String 2 |  |  | 11 | 12 | 23 | 9.6702 | 0.2791
3 | String 3 |  |  | 9 | 12 | 21 | 8.8293 | 0.25483
4 | String 4 |  |  | 10 | 12 | 22 | 9.2498 | 0.26697
5 | String 5 |  |  | 24 | 25 | 49 | 20.6017 | 0.59461
| TOTAL LENGTH: |  |  |  |  | 148
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.59461
1 | String 1 | INVERTER 14 |  | 14 | 17 | 31 | 13.0337 | 0.37618
2 | String 2 |  |  | 25 | 9 | 34 | 14.2951 | 0.41259
3 | String 3 |  |  | 8 | 9 | 17 | 7.1475 | 0.20629
4 | String 4 |  |  | 28 | 31 | 59 | 24.8062 | 0.71596
5 | String 5 |  |  | 29 | 32 | 61 | 25.6471 | 0.74023
| TOTAL LENGTH: |  |  |  |  | 202
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.74023
1 | String 1 | INVERTER 15 |  | 13 | 10 | 23 | 9.6702 | 0.2791
2 | String 2 |  |  | 12 | 10 | 22 | 9.2498 | 0.26697
3 | String 3 |  |  | 7 | 10 | 17 | 7.1475 | 0.20629
4 | String 4 |  |  | 8 | 11 | 19 | 7.9884 | 0.23056
5 | String 5 |  |  | 14 | 15 | 29 | 12.1929 | 0.35191
| TOTAL LENGTH: |  |  |  |  | 110
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.35191
1 | String 1 | INVERTER 16 |  | 13 | 10 | 23 | 9.6702 | 0.2791
2 | String 2 |  |  | 6 | 8 | 14 | 5.8862 | 0.16989
3 | String 3 |  |  | 7 | 8 | 15 | 6.3067 | 0.18202
4 | String 4 |  |  | 13 | 15 | 28 | 11.7724 | 0.33978
5 | String 5 |  |  | 13 | 15 | 28 | 11.7724 | 0.33978
| TOTAL LENGTH: |  |  |  |  | 108
| MAXIMUM VOLTAGE DROP: | [6 empty] | 0.33978

## EARTH STRIP SIZE CALCULATION
EARTH STRIP SIZE CALCULATION
Project name: |  | 400.4kWp
Client Name:
EARTH STRIP CALCULATION
AS PER IS: 3043
| K = | √ ( (Qc (B+20))/δ20) ) ln ( 1+ ( θt-θ1)/(B+θ1) )
Where,
Qc = | Volumetric heat capacity of conductor material ( j/°C mm3)
B = | Reciprocal of temperature coefficient of resistivity at 0°C for the conductor (°C)
δ20 = | Electrical resistivity of conductor material at 20°C (ohm-mm)
θ1 = | Initial temperature of conductor = |  |  |  |  | 50
θt = | Final temperature of Steel conductor = |  |  |  |  | 500
Material constants as per IS-3043-1987 Table-5
|  |  | Steel | Aluminium | Copper
|  | B | 202 | 228 | 234.5
|  | Qc | 0.0038 | 0.0025 | 0.00345
|  | δ20 | 0.000138 | 2.8264e-05 | 1.7241e-05
For GI Strip
| K = | √ ( ( 0.0038 (202 + 20) )/0.000138) ) ln ( 1+ (500-50)/(202 + 50) )
|  |  | K = | 79.1381
DC Side
| No. Of Parallel Strings at Inverter |  |  |  | 40 | Nos
| Current Per String |  |  |  | 9.14 | A
| Total Fault Current at Eight Inverters (If) |  |  |  | 365.6 | A
| Safety Factor (125 %) |  |  |  | 457 | A
| Corrosion Effect (1 % Every for 25 years) |  |  |  | 571.25 | A
Area of Cross Section (A) = Fault Current (If) X Fault Current Time √(t)/ Material Constant (K)
| Area of Cross Section (A) = |  |  | 7.2184 | Sqmm
Where,
| If = | Fault Current |  | 571.25 | Ampere
| t = | Fault Current time |  | 1 | Second
| K = | Material Constant |  | 79.1381
Earth Strip Size Selected |  |  |  | 25 X 3 | Sqmm
AC Side
| No. Of Parallel Inverters (25kW) at ACCB |  |  |  | 8 | Nos
| Current Per Inverter |  |  |  | 36.2 | A
| Total Fault Current at Eight Inverters (If) |  |  |  | 362 | A
| Safety Factor (125 %) |  |  |  | 452.5 | A
| Corrosion Effect (1 % Every for 25 years) |  |  |  | 565.625 | A
Area of Cross Section (A) = Fault Current (If) X Fault Current Time √(t)/ Material Constant (K)
| Area of Cross Section (A) = |  |  | 7.1473 | Sqmm
Where,
| If = | Fault Current |  | 565.625 | Ampere
| t = | Fault Current time |  | 1 | Second
| K = | Material Constant |  | 79.1381
Earth Strip Size Selected |  |  |  | 25 X 3 | Sqmm

## Earthing Calculation
EARTHING CALCULATION
Project name: |  | 400.4kWp
Client Name:
Resistance of Earth electrode as per BS 7430
Considering Maintenance free Earth Pit with bore dia 17.2 mm and 3 mtr long
| R = | 1/2πL [ (ρ - ρc) (loge[8L/D] - 1) + ρc (loge[8L/d] - 1) ]
Where,
rc = | Resistivity of the infill material in ohm-m = |  |  |  | 0.2 | ohm-m
D = | Diameter of the infill material in m = |  |  |  | 0.1 | m
l = | Length of the rod or pipe in m = |  |  |  | 3 | m
d = | Diameter of the rod in m = |  |  |  | 0.017 | m
r = | Resistivity of the soil in (ohm-m) = |  |  |  | 6.34 | ohm-m
|  |  | R = | 1.5266 | ohm
Total electrodes considered for individual AC or DC Earthing = 2 Nos
Effective resistance of electrode (Re) expressed as : |  |  |  |  | 1/Re = 1/R1 + 1/R2
|  |  |  | Re = | ( R1 x R2)/( R1 + R2 )
|  |  |  | = | (1.53x1.53)/(1.53+1.53)
|  |  |  | Re = | 0.765 ohm
SOLAR ARRAY AREA EARTH GRID
Resistance of Earth strip as per IS: 3043 (9.2.3)
DC Side
length of earth strip (25X3mm, GI) is buried in the plant at 100mm depth | [5 empty] | 175 | Meter
|  |  | R = | (100ρ/2πl) loge(2l²/wt)
Where,
| r = | Resistivity of the soil ( ohm-Meter) |  |  | 6.34 | ohm-m
| l = | Length of the strip in cm |  |  | 16000 | cm
| w = | Depth of the burial cm |  |  | 0.3 | cm
| t = | Width of the strip |  |  | 2.5 | cm
|  |  | R = | 0.12835 | ohm
Total Effective Resistance of the System = |  |  |  | Strip Resistance + Effective Resistance of Pit
|  |  | RTotal = | 0.895 ohm
Therefore, According to the Tender Value the Resistance of the Should be smaller than 4 ohm.
AC Side
length of earth strip (25X3mm, GI) is buried in the plant at 100mm depth | [5 empty] | 175 | Meter
|  |  | R = | (100ρ/2πl) loge(2l²/wt)
Where,
| r = | Resistivity of the soil ( ohm-Meter) |  |  | 6.34 | ohm-m
| l = | Length of the strip in cm |  |  | 17500 | cm
| w = | Depth of the burial cm |  |  | 0.3 | cm
| t = | Width of the strip |  |  | 2.5 | cm
|  |  | R = | 0.11838 | ohm
Total Effective Resistance of the System = |  |  |  | Strip Resistance + Effective Resistance of Pit
|  |  | RTotal = | 0.885 ohm
Therefore, According to the Tender Value the Resistance of the Should be smaller than 4 ohm.

## Termination
AC VOLTAGE DROP CALCULATION
Project name: |  | 400.4kWp
Client Name:
FROM MAIN ACCB TO TERMINATION POINT
Solar Plant Specifications:
| Rated kVA |  |  | : | 400
| Rated Voltage (V): |  |  | : | 415
| Rated Current (IL): |  |  | : | 556.49
Cable Parameter (As per Polycab):
Derating factors:
Cable Laid in Ground
| Temperature Correction |  |  | : | 0.9
| Grouping |  |  | : | 1
| Total Derating |  |  | : | 0.9
Continous current of Selected Cable
| Type |  | Size | Current Rating in Ground (Ampere) | Derated Current (Ampere) | Total Current Carrying Capacity of 2 Run Cable
| 3.5C, Al, FRLS Cable |  | 240 Sqmm | 327 | 294.3 | 588.6
Verification of cable sizing according to permissible voltage drop
| Voltage Drop %V (3ϕ): |  |  | = | {√3*IL*L*(R Cosϕ+ X Sinϕ)}*100/(N*V)
| R | = | Conductor Resistace
| X | = | Conductor Reactance
| L | = | Cable Length in KM (kilometer)
| N | = | Number of Runs
| Cos(ϕ) | = | Power Factor |  |  | (Power factor is nearly equal to 1)
| Sin(ϕ) | = | Component of Reactive Power |  |  | (Assumed as Zero)
| IL | = | Rated Current
| V | = | Rated Voltage
SR. NO. | FROM | TO |  | Resistance (R) of Cable (Ohm/Km) | Reactance (X) of Cable (Ohm/Km) | Total Length in (KM) | Number of Run | %Voltage Drop
1 | MAIN ACCB | TERMINATION POINT |  | 0.15 | 0.0876 | 0.02 | 2 | 0.34838