## 1000A
1000 A MCC BUSBAR SIZING CALCULATION
PROJECT | 30 MW POWER PLANT |  | Revision :
CLIENT |  |  | Date :
CONSULTANT |  |  | No. of Sheet -
EPC CONTRACTOR |  |  | https://www.flasysdesign.com/
Document ID |  |  | Email: contact@flasysdesign.com
1 | Input Data
1.1 | Type of Panel | : | Cubical Type
1.2 | System | : | 3PH ,3 Wire / 4 Wire
1.3 | Rated Voltage | : | 415V
1.4 | degree of Protection | : | 50 Hz.
1.5 | Panel Max. Current Rating in Amp (Design) | : | 1000
1.6 | Fault Current & Duration (KA RMS Symmetrical for 1 Sec.) | : | 50
1.7 | Ambient Temperature (Deg. C.) | : | 50
1.8 | Maximum Bus bar Temperature (Deg. C.) | : | 85
1.9 | Maximum Enclosure Temperature (Deg. C.) | : | 70
1.1 | Degree of Protection | : | IP: 52 & IP: 42 for ACB Incomer
1.11 | Bus bar Size for Phase | : | 1 x 1 x 125 x 10 MM
| Bus bar Size for Neutral | : | 1 x 125 x 06 MM
| No. of Runs | : | 1
| No. of times Interleaved | : | 1
| Width of Bus Bar in mm | : | 125
| Thickness of Bus Bar in mm | : | 10
1.12 | Bus bar cross section for Neutral in Sq.mm |  | 750
1.13 | Cross section of Bus bar Selected in Sq. mm | : | 1250
1.14 | Type of Insulator | : | SMC support with ribbed construction
1.15 | Basic Insulation Level:
a | One Minute Power Frequency voltage | : | 2.5KV RMS
1.16 | Painting:
| a. Enclosure Interior & Exterior | : | Epoxy paint RAL-7032, Siemens Grey
| b. Bus bar | : | Heat Shrinkable Sleeved.
1.17 | Minimum Clearance:
| a. Phase to Phase | : | 25 mm
| b. Phase to Earth | : | 20 mm
1.18 | Applicable Standard | : | IS: 8623 Construction
|  | : | IS : 5082 Bus bar
1.19 | Degree of Protection | : | IP: 54 for Indoor & IP: 55 for Outdoor
1.2 | Span Between 2 support | : | 0.5mtr. (500mm)
2 | Bus duct Sizing Calculation for MCC
2.1 | Short Time Thermal Withstand Capability of Bus bar
| Minimum Cross Sectional Area of Busbar (A) In Sq. Inches | = | ( Isc / √T ) / {14 x 10⁴ √log₁₀ [T1 +258)/(T2+258)] }
| Isc = Short Circuit Symmetrical Fault Current in KA | = | 50
| T = Fault duration in Sec | = | 1
| T1 = Initial Temperature of Busbar in Deg.C | = | 85
| T2 = Final Temperature in Deg.C | = | 200
| A = Cross sectional area of busbar in Sq.inches | = | 1.0079
| A in sq.mm = A x 645.16 |  | 650.2257
2.2 | Required cross sectional Area |  | 650.226 Sq.mm for pure aluminium.
2.2 | Actual Cross section of Bus bar Selected (As per Clause1.13) in Sq.mm | = | 1250
2.3 | Conclusion: Conclusion: Conclusion: Conclusion:
The required cross section 650.226 Sq.mm is less than actual cross section 1250 Sq.mm of the bus bar selected. Hence, the bus bar size chosen is safe for the envisaged system.
3 | Bus bar Selection for Continuous Current Rating :
3.1 | Bus bar Selected | : | As per Clause1.11
3.11 | Open air rating of bus bar for 50 Deg. C rise over ambient in Amps. | : | 1850
| No. of times Interleaved (As per Clause1.11) | : | 1 x 1850
| Overall Rating of Bus Bar in Amps. | : | 1850
3.12 | Phase spacing in mm. | : | 150
3.13 | Enclosed Size in (W x D x H ) mm | : | 5500 x 800 x 2400 mm
3.14 | Bus bar Enclosed in (W x D ) mm | : | 800 x 400 mm
3.15 | Design Ambient Temperature | : | 50 Deg. C
3.16 | Maximum allowable temp. rise | : | 35 Deg. C
3.17 | Enclosure Material | : | MS Steel
3.18 | De-rating / Up rating:
a | Ambient correction factor for 35 Deg. Rise | = | 0.9
b | Enclosure correction factor corresponding to bus bar | = | 0.87
c | Enclosure Correction factor Material (MS) | = | 0.9
d | Proximity Effect Factor | = | 0.95
e | Bus bar Configuration Factor | = | 1
g | Combined Correction Factor | = | 0.66946
3.19 | De-rated Current rating of bus bar after applying Correction factor in Amps. | = | 1850 x 0.67
|  | = | 1238.5103
3.2 | Rating of Panel required (As per Clause 1.5) | = | 1000
3.21 | Conclusion :
The de-rated Current rating 1238.51 amp of Panel selected is more than the required current rating 1000 amp of Bus duct Bus bar. Hence, the bus bar size chosen is safe for the envisaged system.
4 | Support Insulator Span Calculation During Short Circuit
4.1 | Fm = Peak Electromagnetic force along the centre line of busbar without enclosure | = | K x 16 x Isc² x 10⁻⁴ / S
a | Isc = Short Circuit Symmetrical Fault Current in KA | = | 50
b | S = Phase spacing in Meter | = | 0.25
c | K = Multiplying factor (s-a)/(a+b) | = | 0.904
| corresponding to a that is 60 corresponding to a that is 60 | = | 0.4 (Reffering to curve K is 0.9)
| Fm (Nm / cm² )Fm (Nm / cm² ) | = | 14400
| Fm ( Kg / cm² ) = (Fm x 0.1019716)Fm ( Kg / cm² ) = (Fm x 0.1019716) | = | 1468.391
4.12 | F = Force acting on top of the insulator | = | Fm (H+h)/4H
a | Where, H = Cantilever Height of insulator in mm | = | 38
b | h = Distance between surface of insulator to centre of Bus bar in mm | = | 75
| F | = | 1091.6328
4.13 | Average span to be addopted in mm | = | Cantilever Strength of insulator / safety factor x F
|  | = | Sk / (SF x F )
a | SK = Cantilever strength of insulator(Kg/cm²)SK = Cantilever strength of insulator(Kg/cm²) | = | 1600
b | SF = Safety factor | = | 2.5
| Length of Span of insulator in mm | = | 586.2777
| Adopted Span is |  | OK
4.4 | Conclusion:
Average span of 586.278 mm is required but span adopted is 500 mm, hence it is safe for the system envisaged.
5 | Temperature Rise Calculation
5.1 | Where, I1=Calculated Rating in Amps (After deration) As per Clause 3.19 | = | 1238.5103
5.2 | I2 = Specified Rating in Amps as per clause 1.5 | = | 1000
5.3 | T1 = Max. Temp. Rise (in Deg.C) Specified | = | 35
5.4 | T2 = Temp. Rise in Deg. C to be calculated as | = | ( I1 / I2 ) = ( T1 / T2)0.61
| T2 | = | T1 / (I1 / I2 )1.64
|  | = | 24.6441
| Calculated Temperature is | = | OK
5.5 | Conclusion :
The Calculated Temperature rise of bus bar is 24.64 Deg. C, which is within the design Specified Temp. 35 Deg. C and it is safe for the System envisaged.

## 630A
630 A MCC BUSBAR SIZING CALCULATION
PROJECT | 30 MW POWER PLANT |  | Revision :
CLIENT |  |  | Date :
CONSULTANT |  |  | No. of Sheet -
EPC CONTRACTOR |  |  | https://www.flasysdesign.com/
Document ID |  |  | Email: contact@flasysdesign.com
1 | Input Data
1.1 | Type of Panel | : | Cubical Type
1.2 | System | : | 3PH ,3 Wire / 4 Wire
1.3 | Rated Voltage | : | 415V
1.4 | degree of Protection | : | 50 Hz.
1.5 | Panel Max. Current Rating in Amp (Design) | : | 630
1.6 | Fault Current & Duration (KA RMS Symmetrical for 1 Sec.) | : | 50
1.7 | Ambient Temperature (Deg. C.) | : | 50
1.8 | Maximum Bus bar Temperature (Deg. C.) | : | 85
1.9 | Maximum Enclosure Temperature (Deg. C.) | : | 70
1.1 | Degree of Protection | : | IP: 52 & IP: 42 for ACB Incomer
1.11 | Bus bar Size for Phase | : | 1 x 1 x 75 x 12 MM
| Bus bar Size for Neutral | : | 1 x 75 x 06 MM
| No. of Runs | : | 1
| No. of times Interleaved | : | 1
| Width of Bus Bar in mm | : | 75
| Thickness of Bus Bar in mm | : | 12
1.12 | Bus bar cross section for Neutral in Sq.mm |  | 450
1.13 | Cross section of Bus bar Selected in Sq. mm | : | 900
1.14 | Type of Insulator | : | SMC support with ribbed construction
1.15 | Basic Insulation Level:
a | One Minute Power Frequency voltage | : | 2.5KV RMS
1.16 | Painting:
| a. Enclosure Interior & Exterior | : | Epoxy paint RAL-7032, Siemens Grey
| b. Bus bar | : | Heat Shrinkable Sleeved.
1.17 | Minimum Clearance:
| a. Phase to Phase | : | 25 mm
| b. Phase to Earth | : | 20 mm
1.18 | Applicable Standard | : | IS: 8623 Construction
|  | : | IS : 5082 Bus bar
1.19 | Degree of Protection | : | IP: 54 for Indoor & IP: 55 for Outdoor
1.2 | Span Between 2 support | : | 0.5mtr. (500mm)
2 | Bus duct Sizing Calculation for MCC
2.1 | Short Time Thermal Withstand Capability of Bus bar
| Minimum Cross Sectional Area of Busbar (A) In Sq. Inches | = | ( Isc / √T ) / {14 x 10⁴ √log₁₀ [T1 +258)/(T2+258)] } ( Isc / √T ) / {14 x 10⁴ √log₁₀ [T1 +258)/(T2+258)] } ( Isc / √T ) / {14 x 10⁴ √log₁₀ [T1 +258)/(T2+258)] } ( Isc / √T ) / {14 x 10⁴ √log₁₀ [T1 +258)/(T2+258)] } ( Isc / √T ) / {14 x 10⁴ √log₁₀ [T1 +258)/(T2+258)] }
| Isc = Short Circuit Symmetrical Fault Current in KA | = | 50
| T = Fault duration in Sec | = | 1
| T1 = Initial Temperature of Busbar in Deg.C | = | 85
| T2 = Final Temperature in Deg.C | = | 200
| A = Cross sectional area of busbar in Sq.inches | = | 1.0079
| A in sq.mm = A x 645.16 |  | 650.2257
2.2 | Required cross sectional Area |  | 650.226 Sq.mm for pure aluminium.
2.2 | Actual Cross section of Bus bar Selected (As per Clause1.13) in Sq.mm | = | 900
2.3 | Conclusion: Conclusion: Conclusion: Conclusion:
The required cross section 650.226 Sq.mm is less than actual cross section 900 Sq.mm of the bus bar selected. Hence, the bus bar size chosen is safe for the envisaged system.
3 | Bus bar Selection for Continuous Current Rating :
3.1 | Bus bar Selected | : | As per Clause1.11
3.11 | Open air rating of bus bar for 50 Deg. C rise over ambient in Amps. | : | 1350
| No. of times Interleaved (As per Clause1.11) | : | 1 x 1350
| Overall Rating of Bus Bar in Amps. | : | 1350
3.12 | Phase spacing in mm. | : | 150
3.13 | Enclosed Size in (W x D x H ) mm | : | 7800 x 800 x 2400 mm
3.14 | Bus bar Enclosed in (W x D ) mm | : | 800 x 400 mm
3.15 | Design Ambient Temperature | : | 50 Deg. C
3.16 | Maximum allowable temp. rise | : | 35 Deg. C
3.17 | Enclosure Material | : | MS Steel
3.18 | De-rating / Up rating:
a | Ambient correction factor for 35 Deg. Rise | = | 0.9
b | Enclosure correction factor corresponding to bus bar | = | 0.87
c | Enclosure Correction factor Material (MS) | = | 0.9
d | Proximity Effect Factor | = | 0.95
e | Bus bar Configuration Factor | = | 1
g | Combined Correction Factor | = | 0.66946
3.19 | De-rated Current rating of bus bar after applying Correction factor in Amps. | = | 1350 x 0.67
|  | = | 903.7777
3.2 | Rating of Panel required (As per Clause 1.5) | = | 630
3.21 | Conclusion :
The de-rated Current rating 903.78 amp of Panel selected is more than the required current rating 630 amp of Bus duct Bus bar. Hence, the bus bar size chosen is safe for the envisaged system.
4 | Support Insulator Span Calculation During Short Circuit
4.1 | Fm = Peak Electromagnetic force along the centre line of busbar without enclosure | = | K x 16 x Isc² x 10⁻⁴ / SK x 16 x Isc² x 10⁻⁴ / SK x 16 x Isc² x 10⁻⁴ / S
a | Isc = Short Circuit Symmetrical Fault Current in KA | = | 50
b | S = Phase spacing in Meter | = | 0.25
c | K = Multiplying factor (s-a)/(a+b) | = | 0.904
| corresponding to a that is 60 corresponding to a that is 60 | = | 0.4 (Reffering to curve K is 0.9)
| Fm (Nm / cm² )Fm (Nm / cm² ) | = | 14400
| Fm ( Kg / cm² ) = (Fm x 0.1019716)Fm ( Kg / cm² ) = (Fm x 0.1019716) | = | 1468.391
4.12 | F = Force acting on top of the insulator | = | Fm (H+h)/4H
a | Where, H = Cantilever Height of insulator in mm | = | 38
b | h = Distance between surface of insulator to centre of Bus bar in mm | = | 75
| F | = | 1091.6328
4.13 | Average span to be addopted in mm | = | Cantilever Strength of insulator / safety factor x F
|  | = | Sk / (SF x F )
a | SK = Cantilever strength of insulator(Kg/cm²)SK = Cantilever strength of insulator(Kg/cm²) | = | 1600
b | SF = Safety factor | = | 2.5
| Length of Span of insulator in mm | = | 586.2777
| Adopted Span is |  | OK
4.4 | Conclusion:
Average span of 586.278 mm is required but span adopted is 500 mm, hence it is safe for the system envisaged.
5 | Temperature Rise Calculation
5.1 | Where, I1=Calculated Rating in Amps (After deration) As per Clause 3.19 | = | 903.7777
5.2 | I2 = Specified Rating in Amps as per clause 1.5 | = | 630
5.3 | T1 = Max. Temp. Rise (in Deg.C) Specified | = | 35
5.4 | T2 = Temp. Rise in Deg. C to be calculated as | = | ( I1 / I2 ) = ( T1 / T2)0.61
| T2 | = | T1 / (I1 / I2 )1.64
|  | = | 19.3662
| Calculated Temperature is | = | OK
5.5 | Conclusion :
The Calculated Temperature rise of bus bar is 19.37 Deg. C, which is within the design Specified Temp. 35 Deg. C and it is safe for the System envisaged.

## 800A
800 A MCC BUSBAR SIZING CALCULATION
PROJECT | 30 MW POWER PLANT |  | Revision :
CLIENT |  |  | Date :
CONSULTANT |  |  | No. of Sheet -
EPC CONTRACTOR |  |  | https://www.flasysdesign.com/
Document ID |  |  | Email: contact@flasysdesign.com
1 | Input Data
1.1 | Type of Panel | : | Cubical Type
1.2 | System | : | 3PH ,3 Wire / 4 Wire
1.3 | Rated Voltage | : | 415V
1.4 | degree of Protection | : | 50 Hz.
1.5 | Panel Max. Current Rating in Amp (Design) | : | 800
1.6 | Fault Current & Duration (KA RMS Symmetrical for 1 Sec.) | : | 50
1.7 | Ambient Temperature (Deg. C.) | : | 50
1.8 | Maximum Bus bar Temperature (Deg. C.) | : | 85
1.9 | Maximum Enclosure Temperature (Deg. C.) | : | 70
1.1 | Degree of Protection | : | IP: 52 & IP: 42 for ACB Incomer
1.11 | Bus bar Size for Phase | : | 1 x 1 x 100 x 10 MM
| Bus bar Size for Neutral | : | 1 x 100 x 06 MM
| No. of Runs | : | 1
| No. of times Interleaved | : | 1
| Width of Bus Bar in mm | : | 100
| Thickness of Bus Bar in mm | : | 10
1.12 | Bus bar cross section for Neutral in Sq.mm |  | 600
1.13 | Cross section of Bus bar Selected in Sq. mm | : | 1000
1.14 | Type of Insulator | : | SMC support with ribbed construction
1.15 | Basic Insulation Level:
a | One Minute Power Frequency voltage | : | 2.5KV RMS
1.16 | Painting:
| a. Enclosure Interior & Exterior | : | Epoxy paint RAL-7032, Siemens Grey
| b. Bus bar | : | Heat Shrinkable Sleeved.
1.17 | Minimum Clearance:
| a. Phase to Phase | : | 25 mm
| b. Phase to Earth | : | 20 mm
1.18 | Applicable Standard | : | IS: 8623 Construction
|  | : | IS : 5082 Bus bar
1.19 | Degree of Protection | : | IP: 54 for Indoor & IP: 55 for Outdoor
1.2 | Span Between 2 support | : | 0.5mtr. (500mm)
2 | Bus duct Sizing Calculation for MCC
2.1 | Short Time Thermal Withstand Capability of Bus bar
| Minimum Cross Sectional Area of Busbar (A) In Sq. Inches | = | ( Isc / √T ) / {14 x 10⁴ √log₁₀ [T1 +258)/(T2+258)] } ( Isc / √T ) / {14 x 10⁴ √log₁₀ [T1 +258)/(T2+258)] } ( Isc / √T ) / {14 x 10⁴ √log₁₀ [T1 +258)/(T2+258)] } ( Isc / √T ) / {14 x 10⁴ √log₁₀ [T1 +258)/(T2+258)] } ( Isc / √T ) / {14 x 10⁴ √log₁₀ [T1 +258)/(T2+258)] }
| Isc = Short Circuit Symmetrical Fault Current in KA | = | 50
| T = Fault duration in Sec | = | 1
| T1 = Initial Temperature of Busbar in Deg.C | = | 85
| T2 = Final Temperature in Deg.C | = | 200
| A = Cross sectional area of busbar in Sq.inches | = | 1.0079
| A in sq.mm = A x 645.16 |  | 650.2257
2.2 | Required cross sectional Area |  | 650.226 Sq.mm for pure aluminium.
2.2 | Actual Cross section of Bus bar Selected (As per Clause1.13) in Sq.mm | = | 1000
2.3 | Conclusion: Conclusion: Conclusion: Conclusion:
The required cross section 650.226 Sq.mm is less than actual cross section 1000 Sq.mm of the bus bar selected. Hence, the bus bar size chosen is safe for the envisaged system.
3 | Bus bar Selection for Continuous Current Rating :
3.1 | Bus bar Selected | : | As per Clause1.11
3.11 | Open air rating of bus bar for 50 Deg. C rise over ambient in Amps. | : | 1500
| No. of times Interleaved (As per Clause1.11) | : | 1 x 1500
| Overall Rating of Bus Bar in Amps. | : | 1500
3.12 | Phase spacing in mm. | : | 150
3.13 | Enclosed Size in (W x D x H ) mm | : | 4400 x 800 x 2400 mm
3.14 | Bus bar Enclosed in (W x D ) mm | : | 800 x 400 mm
3.15 | Design Ambient Temperature | : | 50 Deg. C
3.16 | Maximum allowable temp. rise | : | 35 Deg. C
3.17 | Enclosure Material | : | MS Steel
3.18 | De-rating / Up rating:
a | Ambient correction factor for 35 Deg. Rise | = | 0.9
b | Enclosure correction factor corresponding to bus bar | = | 0.87
c | Enclosure Correction factor Material (MS) | = | 0.9
d | Proximity Effect Factor | = | 0.95
e | Bus bar Configuration Factor | = | 1
g | Combined Correction Factor | = | 0.66946
3.19 | De-rated Current rating of bus bar after applying Correction factor in Amps. | = | 1500 x 0.67
|  | = | 1004.1975
3.2 | Rating of Panel required (As per Clause 1.5) | = | 800
3.21 | Conclusion :
The de-rated Current rating 1004.19 amp of Panel selected is more than the required current rating 800 amp of Bus duct Bus bar. Hence, the bus bar size chosen is safe for the envisaged system.
4 | Support Insulator Span Calculation During Short Circuit
4.1 | Fm = Peak Electromagnetic force along the centre line of busbar without enclosure | = | K x 16 x Isc² x 10⁻⁴ / SK x 16 x Isc² x 10⁻⁴ / SK x 16 x Isc² x 10⁻⁴ / S
a | Isc = Short Circuit Symmetrical Fault Current in KA | = | 50
b | S = Phase spacing in Meter | = | 0.25
c | K = Multiplying factor (s-a)/(a+b) | = | 0.904
| corresponding to a that is 60 corresponding to a that is 60 | = | 0.4 (Reffering to curve K is 0.9)
| Fm (Nm / cm² )Fm (Nm / cm² ) | = | 14400
| Fm ( Kg / cm² ) = (Fm x 0.1019716)Fm ( Kg / cm² ) = (Fm x 0.1019716) | = | 1468.391
4.12 | F = Force acting on top of the insulator | = | Fm (H+h)/4H
a | Where, H = Cantilever Height of insulator in mm | = | 38
b | h = Distance between surface of insulator to centre of Bus bar in mm | = | 75
| F | = | 1091.6328
4.13 | Average span to be addopted in mm | = | Cantilever Strength of insulator / safety factor x F
|  | = | Sk / (SF x F )
a | SK = Cantilever strength of insulator(Kg/cm²)SK = Cantilever strength of insulator(Kg/cm²) | = | 1600
b | SF = Safety factor | = | 2.5
| Length of Span of insulator in mm | = | 586.2777
| Adopted Span is |  | OK
4.4 | Conclusion:
Average span of 586.278 mm is required but span adopted is 500 mm, hence it is safe for the system envisaged.
5 | Temperature Rise Calculation
5.1 | Where, I1=Calculated Rating in Amps (After deration) As per Clause 3.19 | = | 1004.1975
5.2 | I2 = Specified Rating in Amps as per clause 1.5 | = | 800
5.3 | T1 = Max. Temp. Rise (in Deg.C) Specified | = | 35
5.4 | T2 = Temp. Rise in Deg. C to be calculated as | = | ( I1 / I2 ) = ( T1 / T2)0.61
| T2 | = | T1 / (I1 / I2 )1.64
|  | = | 24.1075
| Calculated Temperature is | = | OK
5.5 | Conclusion :
The Calculated Temperature rise of bus bar is 24.11 Deg. C, which is within the design Specified Temp. 35 Deg. C and it is safe for the System envisaged.