## D.B. detail
BUILDING NAME:
|  |  | PANEL NAME | [7 empty] | MOUNTING |  |  |  | WALL |  | 380/220V ,3PH.4W,SN
|  |  | LOCATION | [7 empty] | ROOM NO. | [10 empty] | TRIP | FRAM
|  |  | FEEDER ENTRY |  |  | BOTTOM |  |  |  |  | NO. OF WAYS |  |  |  | 16 |  | MAIN CIRCUIT BREAKER |  |  |  |  | 250 | 250 | AMP.
CONDUITE | WIRE | CCT | DESCRIPTION | CONNECTED LOAD |  |  | CIRCUIT BREAKER |  |  | DERI. FAC. | DEMAND | R. | Y. | B. | DEMAND | DERI. FAC. | CIRCUIT BREAKER |  |  | CONNECTED LOAD |  |  | DESCRIPTION | CCT | WIRE | CONDUITE
SIZE | SIZE | NO. |  | PH."R" | PH."Y" | PH."B" | NO. OF | TRIP | F.R.A. |  | LOAD |  |  |  | LOAD |  | F.R.A. | TRIP | NO. OF | PH."R" | PH."Y" | PH."B" |  | NO. | SIZE | SIZE
MM | MM2 |  |  | VA | VA | VA | POLES | AMP. | AMP. |  | AMP. |  |  |  | AMP. |  | AMP. | AMP. | POLES | VA | VA | VA |  |  | MM2 | MM
12 | 2x25+10E | 1 | [9 empty] | * | [11 empty] | 2 | 2x25+10E
|  | 3 | [10 empty] | * | [10 empty] | 4
|  | 5 | [11 empty] | * | [9 empty] | 6
|  | 7 | [9 empty] | * | [11 empty] | 8
|  | 9 | [10 empty] | * | [10 empty] | 10
38P.V.C. |  | 11 | [11 empty] | * | [9 empty] | 12
|  | 13 | [9 empty] | * | [11 empty] | 14
|  | 15 | [10 empty] | * | [10 empty] | 16
|  | 17 | [11 empty] | * | [9 empty] | 18
|  | 19 | [9 empty] | * | [11 empty] | 20
|  | 21 | [10 empty] | * | [10 empty] | 22
|  | 23 | [11 empty] | * | [9 empty] | 24
|  | 25 | [9 empty] | * | [11 empty] | 26
|  | 27 | [10 empty] | * | [10 empty] | 28
|  | 29 | [11 empty] | * | [9 empty] | 30
|  | 31 | [9 empty] | * | [11 empty] | 32
|  | 33 | [10 empty] | * | [10 empty] | 34
|  | 35 | [11 empty] | * | [9 empty] | 36
|  | 37 | [9 empty] | * | [11 empty] | 38
|  | 39 | [10 empty] | * | [10 empty] | 40
|  | 41 | [11 empty] | * | [9 empty] | 42
|  | 43 | [9 empty] | * | [11 empty] | 44
|  | 45 | [10 empty] | * | [10 empty] | 46
|  | 47 |  | 30600 | 28200 | 29600 | [7 empty] | * | [5 empty] | 29600 | 31200 | 22800 |  | 48
| SUB. TOTA CONNECTED LOAD V.A. |  |  | 30600 | 28200 | 29600 | [13 empty] | 29600 | 31200 | 22800 | SUB. TOTA CONNECTED LOAD V.A.
| SUB. TOTA DEMAND LOAD |  |  | 22338 | 20586 | 21608 | [13 empty] | 21608 | 22776 | 16644 | SUB. TOTA DEMAND LOAD
| TOTAL CONNECTED LOAD |  |  |  | 172 |  | K.V.A. |  |  |  | 1CABLE = | [5 empty] | 190.7633 |  | AMP. |  |  | NOTE:
| DEMAND FACTOR |  |  |  | 0.73
| TOTAL DEMAND LOAD |  |  |  | 125.56 |  | K.V.A. |  |  |  | CABLE SIZE = |  |  |  |  | 4X300+70EPVC SINGL CORE CABLE

## Laminaire cal.
0
GROUND FLOOR
Room NO. | LIGHTING
| L | W | A | h | K * | Type | Selected Laminaire Specs. | Rated Fluxe | Lamp/lami Z | Lumi. FluxQ | Lampe Power | Utaliation Factor B* | Maintenance Factor V* | NO. of Laminaire n* | Actual NO. N | Actual Fluxe e* | Total power
EN /LOOPY | 18 | 8 | 144 | 3 | 1.8462 | loppy | Recessed Circular Modular Laminaire with Compact Fluorecsent Lamp 36w warm wight | 300 | 1 | 2800 | 36 | 48 | 0.8 | 40.1786 | 27 | 201.6 | 972
Hall Part | 18 | 8 | 144 | 3 | 1.8462 | Hall | Recessed Modular Fluorescent Laminaire with brightness louvers (reflection) with Fluorecsent Lamp 4x18w warm wight | 200 | 4 | 1450 | 21 | 51 | 0.8 | 12.1704 | 12 | 197.2 | 1008
| 7.2 | 5.6 | 40.32 | 2 | 1.575 | Office |  | 300 | 4 | 1450 | 21 | 59 | 0.8 | 4.4185 | 6 | 407.381 | 504
| 9.3 | 3.6 | 33.48 | 2 | 1.2977 | Office |  | 300 | 4 | 1450 | 21 | 58 | 0.8 | 3.7322 | 4 | 321.5293 | 336
| 6.75 | 5.7 | 38.475 | 2 | 1.5452 | Office |  | 300 | 4 | 1450 | 21 | 59 | 0.8 | 4.2163 | 4 | 284.6108 | 336
| 6.75 | 4.5 | 30.375 | 2 | 1.35 | Office |  | 300 | 4 | 1450 | 21 | 58 | 0.8 | 3.386 | 4 | 354.3967 | 336
| 6.75 | 5.7 | 38.475 | 2 | 1.5452 | Office |  | 300 | 4 | 1450 | 21 | 59 | 0.8 | 4.2163 | 4 | 284.6108 | 336
| 8.3 | 6.4 | 53.12 | 2 | 1.8068 | Office |  | 500 | 4 | 1450 | 21 | 61.5 | 0.8 | 9.3075 | 9 | 483.4789 | 756
| 8 | 3 | 24 | 2 | 1.0909 | Office |  | 300 | 4 | 1450 | 21 | 57.5 | 0.8 | 2.6987 | 3 | 333.5 | 252
| 6.75 | 4.5 | 30.375 | 2 | 1.35 | Office |  | 300 | 4 | 1450 | 21 | 58 | 0.8 | 3.386 | 4 | 354.3967 | 336
| 2.6 | 3 | 7.8 | 2 | 0.69643 | Office |  | 300 | 4 | 1450 | 21 | 51 | 0.8 | 0.98884 | 1 | 303.3846 | 84
| 8.3 | 4.4 | 36.52 | 2 | 1.4378 | Office |  | 300 | 4 | 1450 | 21 | 59 | 0.8 | 4.002 | 4 | 299.8467 | 336
| 12 | 3 | 36 | 2 | 1.2 | Waiting |  | 150 | 4 | 1450 | 21 | 57.5 | 0.8 | 2.024 | 3 | 222.3333 | 252
| K *=A/((L+W)*H) |  | h=H-hs-wl |  |  | v*=.8normal,.7high,.6special |  | B*From luminaire Table |  |  |  | n*=E*A*100/(Z*Q*B*v) |  | e*=N*Z*Q*B*V/(A*100)
LOWER BASE.FLOOR
Room NO. | LIGHTING
| L | W | A | h | K * | Type | Selected Laminaire Specs. | Rated Fluxe | Lamp/lami Z | Lumi. FluxQ | Lampe Power | Utaliation Factor B* | Maintenance Factor V* | NO. of Laminaire n* | Actual NO. N | Actual Fluxe e* | Total power
EN /LOOPY | 18 | 8 | 144 | 3 | 1.8462 | Parking | Surface Mounted Modular Fluorescent Laminaire with brightness louvers (reflection) with Fluorecsent Lamp 2x36w warm wight | 100 | 2 | 3100 | 36 | 54 | 0.8 | 5.3763 | 6 | 111.6 | 432
| 7.25 | 7.25 | 52.5625 | 3 | 1.2083 | Lifts lobby | Recessed Circular Modular Laminaire with Compact Fluorecsent Lamp 36w warm wight | 150 | 1 | 2800 | 36 | 54 | 0.8 | 6.5182 | 7 | 161.0882 | 252
| K *=A/((L+W)*H) |  | h=H-hs-wl |  |  | v*=.8normal,.7high,.6special |  | B*From luminaire Table |  |  |  | n*=E*A*100/(Z*Q*B*v) |  | e*=N*Z*Q*B*V/(A*100)

## Table1
0
Table1
Effective resistance per unit length of plastic -shethed cables NYM and
power cables NYY,NYCY and NYCWY with copper conductors.
Number of | D.C.resistance | Ohmic resistance | Inductive | Effective resistance per unit length |  |  | R'LCOSФ+X'LSINФ
conductors and | at 70 °c | at 70 °c | Reactance | at COS Ф
cross section | R'_ | R'L | X'L | 0.95 | 0.9 | 0.8 | 0.7 | 0.6
mm2 | Ω/Km | Ω/Km | Ω/Km | Ω/Km | Ω/Km | Ω/Km | Ω/Km | Ω/Km
4X1.5 | 14.47 | 14.47 | 0.115 | 13.8 | 13.1 | 11.65 | 10.2 | 8.77
4X2.5 | 8.71 | 8.71 | 0.11 | 8.31 | 7.89 | 7.03 | 6.18 | 5.31
4X4 | 5.45 | 5.45 | 0.107 | 5.21 | 4.95 | 4.42 | 3.89 | 3.36
4X6 | 3.62 | 3.62 | 0.1 | 3.47 | 3.3 | 2.96 | 2.61 | 2.25
4X10 | 2.16 | 2.16 | 0.094 | 2.08 | 1.99 | 1.78 | 1.85 | 1.37
4X16 | 1.36 | 1.36 | 0.09 | 1.32 | 1.26 | 1.14 | 1.02 | 0.888
4X25 | 0.863 | 0.863 | 0.086 | 0.847 | 0.814 | 0.742 | 0.666 | 0.587
4X35 | 0.627 | 0.627 | 0.083 | 0.622 | 0.6 | 0.55 | 0.498 | 0.443
4X50 | 0.463 | 0.463 | 0.083 | 0.466 | 0.453 | 0.42 | 0.38 | 0.344
4X70 | 0.621 | 0.621 | 0.082 | 0.331 | 0.326 | 0.306 | 0.283 | 0.258
4X95 | 0.231 | 0.232 | 0.082 | 0.246 | 0.254 | 0.235 | 0.221 | 0.205
4X120 | 0.183 | 0.184 | 0.08 | 0.2 | 0.2 | 0.195 | 0.168 | 0.174
4X150 | 0.149 | 0.15 | 0.08 | 0.168 | 0.17 | 0.178 | 0.162 | 0.154
4X185 | 0.118 | 0.1201 | 0.08 | 0.139 | 0.143 | 0.144 | 0.141 | 0.136
4X240 | 0.0901 | 0.0922 | 0.079 | 0.112 | 0.117 | 0.121 | 0.121 | 0.119
4X300 | 0.0718 | 0.0745 | 0.079 | 0.0954 | 0.101 | 0.107 | 0.109 | 0.108

## Table2
0
Table2
Effective resistance per unit length of plastic -shethed cables NYM and
power cables NYY,NYCY and NYCWY with aluminum conductors.
Number of | D.C.resistance | Ohmic resistance | Inductive | Effective resistance per unit length |  |  | R'LCOSФ+X'LSINФ
conductors and | at 20 °c | at 70 °c | Reactance | at COS Ф
cross section | R'_ | R'L | X'L | 0.95 | 0.9 | 0.8 | 0.7 | 0.6
mm2 | Ω/Km | Ω/Km | Ω/Km | Ω/Km | Ω/Km | Ω/Km | Ω/Km | Ω/Km
4X10 | 3.08 | 3.3 | 0.094 | 3.1644 | 3.011 | 2.6964 | 2.3771 | 2.0552
4X16 | 1.91 | 2.29 | 0.08649 | 2.2025 | 2.0987 | 1.8839 | 1.6648 | 1.4432
4X25 | 1.2 | 1.44 | 0.08533 | 1.3946 | 1.3332 | 1.2032 | 1.0689 | 0.93226
4X35 | 0.868 | 1.043 | 0.07869 | 1.0154 | 0.973 | 0.88161 | 0.7863 | 0.68875
4X50 | 0.641 | 0.771 | 0.078588 | 0.75699 | 0.72816 | 0.66395 | 0.59582 | 0.52547
4X70 | 0.443 | 0.553 | 0.05075 | 0.5412 | 0.51982 | 0.47285 | 0.42334 | 0.3724
4X95 | 0.32 | 0.385 | 0.076526 | 0.38965 | 0.37986 | 0.35392 | 0.32415 | 0.29222
4X120 | 0.253 | 0.305 | 0.074459 | 0.313 | 0.30696 | 0.28868 | 0.26667 | 0.24257
4X150 | 0.206 | 0.249 | 0.073107 | 0.25938 | 0.25597 | 0.24306 | 0.22651 | 0.20789
4X185 | 0.164 | 0.199 | 0.073379 | 0.21196 | 0.21109 | 0.20323 | 0.1917 | 0.1781
4X240 | 0.125 | 0.151 | 0.07187 | 0.16652 | 0.1681 | 0.16512 | 0.15845 | 0.1497
4X300 | 0.1 | 0.123 | 0.071751 | 0.13925 | 0.14198 | 0.14145 | 0.13734 | 0.1312

## cable cal 1ph
0
ELECTRICAL CALCULATION
Project name: |  | WAHAT AL KHARTOUM |  |  |  | Date:
Project no.: | [5 empty] | Designer: | Mohammed moustafa
* LOAD INFORMATION
LOAD REFERENCE
VOLTAGE USED | [6 empty] | 220 | V
NO.OF PHASES | [6 empty] | 1 | PHASES
CONTINUOUS LOAD IN KVA | [6 empty] | 2.5 | KVA
CONTINUOUS LOAD IN AMPS | [6 empty] | 11.3636 | AMPS
CIRCUIT BREAKER AMPS
ICB = Ia x B/A
Ia | Actual full load current or (RMS)current | [5 empty] | 11.3636
A | Ambient temperature factor |  |  |  | at 50 °C |  | 0.9
B | Safety factor | [5 empty] | 1.1
IC.B | [6 empty] | 13.8889 | AMPS
CORRECT SIZE CIRCUIT BREAKER AMPS | [6 empty] | 20 | AMPS
CABLE SELECTION |  |  | ACC to NEC
| We planning to use cable with size | [5 empty] | 3 | mm2
Cable current rating before the correction factors
| according to NEC for one copper cable XLPE inslated&PVCsheahed. | [5 empty] | 21 | AMPS
Correction factors:
| Ambient Temperature factor | [5 empty] | 0.85
| Grouping factor | [5 empty] | 0.8
| Cable current rating after the correction factors | [5 empty] | 14.28 | AMPS
| NO. of cables |  | N\ |  |  |  | 0.97261
Actual | NO. of cables |  | N |  |  |  | 1
| Cable size after correction factors |  |  | 2x3 |  | mm2
| Length of cable per kilometer |  |  | L |  |  | 0.02
VOLTAGE DROP
| R'LCOSФ+X'LSINФ from table (1) |  |  |  |  | = | 7.03
| Voltage drop ∆V = |  | 2*I*L* | (R'LCOSФ+X'LSINФ)/N
|  | = |  |  |  |  | 3.1955 | V
| Voltage drop%= | [5 empty] | 1.4525
CABLE SELECTION |  |  | ACC to VDE
| Voltage drop= |  | 2*I*L* | (R'LCOSФ+X'LSINФ)
|  | ∆V Shall not exdeed 3-5% = |  |  |  |  | 6.6 | V
|  | (R'LCOSФ+X'LSINФ) = |  |  | ∆V /(2*I*L*)
|  |  |  | = |  |  | 14.52
| Ambient Temperature factor |  |  | = |  |  | 0.85
| Grouping factor |  |  | = |  |  | 0.8
|  | (R'LCOSФ+X'LSINФ) after factors |  |  |  | = | 9.8736
| No of cables |  |  | = |  |  | 0.712
0
ELECTRICAL CALCULATION
Project name: |  | WAHAT AL KHARTOUM |  |  |  | Date:
Project no.: | [5 empty] | Designer: | Mohammed moustafa
* LOAD INFORMATION
LOAD REFERENCE
VOLTAGE USED | [6 empty] | 220 | V
NO.OF PHASES | [6 empty] | 1 | PHASES
CONTINUOUS LOAD IN KVA | [6 empty] | 2.5 | KVA
CONTINUOUS LOAD IN AMPS | [6 empty] | 11.3636 | AMPS
CIRCUIT BREAKER AMPS
IC.B=Ia xB / A
Ia | Actual full load current or (RMS)current | [5 empty] | 11.3636
A | Ambient temperature factor |  |  |  | at 50 °C |  | 0.9
B | Safety factor | [5 empty] | 1.1
IC.B | [6 empty] | 13.8889 | AMPS
CORRECT SIZE CIRCUIT BREAKER AMPS | [6 empty] | 20 | AMPS
CABLE SELECTION |  |  | ACC to NEC
| We planning to use cable with size | [5 empty] | 3 | mm2
Cable current rating before the correction factors
| according to NEC for one copper cable XLPE inslated&PVCsheahed. | [5 empty] | 21 | AMPS
Correction factors:
| Ambient Temperature factor | [5 empty] | 0.85
| Grouping factor | [5 empty] | 0.8
| Cable current rating after the correction factors | [5 empty] | 14.28 | AMPS
| NO. of cables |  | N\ |  |  |  | 0.97261
Actual | NO. of cables |  | N |  |  |  | 1
| Cable size after correction factors |  |  | 2x3 |  | mm2
| Length of cable per kilometer |  |  | L |  |  | 0.02
VOLTAGE DROP
| R'LCOSФ+X'LSINФ from table (1) |  |  |  |  | = | 7.03
| Voltage drop ∆V = |  | 2*I*L* | (R'LCOSФ+X'LSINФ)/N
|  | = |  |  |  |  | 3.1955 | V
| Voltage drop%= | [5 empty] | 1.4525
CABLE SELECTION |  |  | ACC to VDE
| Voltage drop= |  | 2*I*L* | (R'LCOSФ+X'LSINФ)
|  | ∆V Shall not exdeed 3-5% = |  |  |  |  | 6.6 | V
|  | (R'LCOSФ+X'LSINФ) = |  |  | ∆V /(2*I*L*)
|  |  |  | = |  |  | 14.52
| Ambient Temperature factor |  |  | = |  |  | 0.85
| Grouping factor |  |  | = |  |  | 0.8
|  | (R'LCOSФ+X'LSINФ) after factors |  |  |  | = | 9.8736
| No of cables |  |  | = |  |  | 0.712
0
ELECTRICAL CALCULATION
Project name: |  | WAHAT AL KHARTOUM |  |  |  | Date:
Project no.: | [5 empty] | Designer: | Mohammed moustafa
* LOAD INFORMATION
LOAD REFERENCE
VOLTAGE USED | [6 empty] | 220 | V
NO.OF PHASES | [6 empty] | 1 | PHASES
CONTINUOUS LOAD IN KVA | [6 empty] | 2.5 | KVA
CONTINUOUS LOAD IN AMPS | [6 empty] | 11.3636 | AMPS
CIRCUIT BREAKER AMPS
IC.B=Ia xB / A
Ia | Actual full load current or (RMS)current | [5 empty] | 11.3636
A | Ambient temperature factor |  |  |  | at 50 °C |  | 0.9
B | Safety factor | [5 empty] | 1.1
IC.B | [6 empty] | 13.8889 | AMPS
CORRECT SIZE CIRCUIT BREAKER AMPS | [6 empty] | 20 | AMPS
CABLE SELECTION |  |  | ACC to NEC
| We planning to use cable with size | [5 empty] | 3 | mm2
Cable current rating before the correction factors
| according to NEC for one copper cable XLPE inslated&PVCsheahed. | [5 empty] | 21 | AMPS
Correction factors:
| Ambient Temperature factor | [5 empty] | 0.85
| Grouping factor | [5 empty] | 0.8
| Cable current rating after the correction factors | [5 empty] | 14.28 | AMPS
| NO. of cables |  | N\ |  |  |  | 0.97261
Actual | NO. of cables |  | N |  |  |  | 1
| Cable size after correction factors |  |  | 2x3 |  | mm2
| Length of cable per kilometer |  |  | L |  |  | 0.02
VOLTAGE DROP
| R'LCOSФ+X'LSINФ from table (1) |  |  |  |  | = | 7.03
| Voltage drop ∆V = |  | 2*I*L* | (R'LCOSФ+X'LSINФ)/N
|  | = |  |  |  |  | 3.1955 | V
| Voltage drop%= | [5 empty] | 1.4525
CABLE SELECTION |  |  | ACC to VDE
| Voltage drop= |  | 2*I*L* | (R'LCOSФ+X'LSINФ)
|  | ∆V Shall not exdeed 3-5% = |  |  |  |  | 6.6 | V
|  | (R'LCOSФ+X'LSINФ) = |  |  | ∆V /(2*I*L*)
|  |  |  | = |  |  | 14.52
| Ambient Temperature factor |  |  | = |  |  | 0.85
| Grouping factor |  |  | = |  |  | 0.8
|  | (R'LCOSФ+X'LSINФ) after factors |  |  |  | = | 9.8736
| No of cables |  |  | = |  |  | 0.712

## Cable cal.3ph
0
ELECTRICAL CALCULATION
Project name: |  | WAHAT AL KHARTOUM |  |  |  | Date:
Project no.: | [5 empty] | Designer: | Mohammed moustafa
* LOAD INFORMATION
LOAD REFERENCE | [6 empty] | TRANSFORMER
VOLTAGE USED | [6 empty] | 380 | V
NO.OF PHASES | [6 empty] | 3 | PHASES | KW | KVA
CONTINUOUS LOAD IN KVA | [6 empty] | 630 | KVA | 80 | 100
CONTINUOUS LOAD IN AMPS | [6 empty] | 957.1859 | AMPS
CIRCUIT BREAKER AMPS
ICB = Ia x B/A
Ia | Actual full load current or (RMS)current | [5 empty] | 957.1859
A | Ambient temperature factor |  |  |  | at 50 °C |  | 0.9
B | Safety factor | [5 empty] | 1.1
IC.B | [6 empty] | 1169.8938 | AMPS
CORRECT SIZE CIRCUIT BREAKER AMPS | [6 empty] | 1200 | AMPS
CABLE SELECTION |  |  | ACC to NEC
| We planning to use cable with size | [5 empty] | 240 | mm2
Cable current rating before the correction factors
| according to NEC for one copper cable XLPE inslated&PVCsheahed. | [5 empty] | 374 | AMPS
Correction factors:
| Ambient Temperature factor | [5 empty] | 0.85
| Grouping factor | [5 empty] | 0.9
| Cable current rating after the correction factors | [5 empty] | 286.11 | AMPS
| NO. of cables |  | N\ |  |  |  | 4.089
Actual | NO. of cables |  | N |  |  |  | 4
| Cable size after correction factors |  |  | 4(3x240+120+120) |  | mm2
| Length of cable per kilometer |  |  | L |  |  | 0.05
VOLTAGE DROP
| R'LCOSФ+X'LSINФ from table (1) |  |  |  |  | = | 0.121
| Voltage drop ∆V = |  | √3*I*L* | (R'LCOSФ+X'LSINФ)/N
|  | = |  |  |  |  | 2.5076 | V
| Voltage drop%= | [5 empty] | 0.6599
CABLE SELECTION |  |  | ACC to VDE
| Voltage drop= |  | √3*I*L* | (R'LCOSФ+X'LSINФ)
|  | ∆V Shall not exdeed 3-5% = |  |  |  |  | 11.4 | V
|  | (R'LCOSФ+X'LSINФ) = |  |  | ∆V /(√3*I*L*)
|  |  |  | = |  |  | 0.13752
| Ambient Temperature factor |  |  | = |  |  | 0.85
| Grouping factor |  |  | = |  |  | 0.8
|  | (R'LCOSФ+X'LSINФ) after factors |  |  |  | = | 0.093514
| No of cables |  |  | = |  |  | 1.2939
Az ZOUR POWER STATION
ELECTRICAL CALCULATION
Project name: |  | Az ZOUR POWER STATION |  |  |  | Date:
Project no.: | [5 empty] | Designer: | Mohammed moustafa
* LOAD INFORMATION
LOAD REFERENCE | [5 empty] | 2NOS | pumps in DB-USG PUMP
VOLTAGE USED | [6 empty] | 22000 | V
NO.OF PHASES | [6 empty] | 3 | PHASES
CONTINUOUS LOAD IN KVA | [6 empty] | 17500 | KVA
CONTINUOUS LOAD IN AMPS | [6 empty] | 459.2558 | AMPS
CIRCUIT BREAKER AMPS
ICB = Ia x B/A
Ia | Actual full load current or (RMS)current | [5 empty] | 459.2558
A | Ambient temperature factor |  |  |  | at 50 °C |  | 0.8
B | Safety factor | [5 empty] | 1.05
IC.B | [6 empty] | 602.7733 | AMPS
CORRECT SIZE CIRCUIT BREAKER AMPS | [6 empty] | 630 | AMPS
CABLE SELECTION |  |  | ACC toIEC
| We planning to use cable with size | [5 empty] | 500 | mm2
Cable current rating before the correction factors
| according toIEC for one copper cable XLPE inslated&PVCsheathed.8.7/15KV | [5 empty] | 651 | AMPS
Correction factors:
| Ambient Temperature factor | [5 empty] | 0.8
| Grouping factor | [5 empty] | 1
| Cable current rating after the correction factors | [5 empty] | 520.8 | AMPS
| NO. of cables |  | N\ |  |  |  | 1.1574
Actual | NO. of cables |  | N |  |  |  | 1
| Cable size after correction factors |  |  | 1X3X | 500 | mm2
| Length of cable per kilometer |  |  | L |  |  | 4.2 | kilometer
VOLTAGE DROP
| R'LCOSФ+X'LSINФ SEE CAL. BLOW |  |  |  |  | = | 0.039277
| Voltage drop ∆V = |  | √3*I*L* | (R'LCOSФ+X'LSINФ)/N
|  | = |  |  |  |  | 131.223 | V
| Voltage drop%= | [5 empty] | 0.59647
DATA FOR | 500 | mm2
L=mh/km |  | X=ω*L*10-3 |  | Ω/Km
ω=2πF
INDUCTANCE | 0.000406 | 3.1416 | 0.00012755 | SINФ= | 0.6 | 7.6529e-05 | X'LSINФ
RESISTANCE |  |  | 0.049 | COSФ= | 0.8 | 0.0392 | R'LCOSФ
[6 empty] | 0.039277 | R'LCOSФ+X'LSINФ
Az ZOUR POWER STATION
ELECTRICAL CALCULATION
Project name: |  | Az ZOUR POWER STATION |  |  |  | Date:
Project no.: | [5 empty] | Designer: | Mohammed moustafa
* LOAD INFORMATION
LOAD REFERENCE | [6 empty] | pb-USG
VOLTAGE USED | [6 empty] | 415 | V
NO.OF PHASES | [6 empty] | 3 | PHASES
CONTINUOUS LOAD IN KVA | [6 empty] | 575 | KVA
CONTINUOUS LOAD IN AMPS | [6 empty] | 799.9431 | AMPS
CIRCUIT BREAKER AMPS
ICB = Ia x B/A
Ia | Actual full load current or (RMS)current | [5 empty] | 799.9431
A | Ambient temperature factor |  |  |  | at 50 °C |  | 0.8
B | Safety factor | [5 empty] | 1.1
IC.B | [6 empty] | 1099.9217 | AMPS
CORRECT SIZE CIRCUIT BREAKER AMPS | [6 empty] | 1200 | AMPS
CABLE SELECTION |  |  | ACC to NEC
| We planning to use cable with size | [5 empty] | 300 | mm2
Cable current rating before the correction factors
| according toIEC for one aluminum cable PVC inslated&PVCsheathed. | [5 empty] | 320 | AMPS
Correction factors:
| Ambient Temperature factor | [5 empty] | 0.8
| Grouping factor | [5 empty] | 1
| Cable current rating after the correction factors | [5 empty] | 256 | AMPS
| NO. of cables |  | N\ |  |  |  | 4.2966
Actual | NO. of cables |  | N |  |  |  | 4
| Cable size after correction factors |  |  | 4X(3x300+150+150) |  | mm2
| Length of cable per kilometer |  |  | L |  |  | 0.1
VOLTAGE DROP
| R'LCOSФ+X'LSINФ from table (1) |  |  |  |  | = | 0.107
| Voltage drop ∆V = |  | √3*I*L* | (R'LCOSФ+X'LSINФ)/N
|  | = |  |  |  |  | 3.7064 | V
| Voltage drop%= | [5 empty] | 0.89312
CABLE SELECTION |  |  | ACC to VDE
| Voltage drop= |  | √3*I*L* | (R'LCOSФ+X'LSINФ)
|  | ∆V Shall not exdeed 3-5% = |  |  |  |  | 12.45 | V
|  | (R'LCOSФ+X'LSINФ) = |  |  | ∆V /(√3*I*L*)
|  |  |  | = |  |  | 0.089854
| Ambient Temperature factor |  |  | = |  |  | 0.85
| Grouping factor |  |  | = |  |  | 0.8
|  | (R'LCOSФ+X'LSINФ) after factors |  |  |  | = | 0.061101
| No of cables |  |  | = |  |  | 1.7512