## Sheet2
By | [20 empty] | Project :
Date |  | 2025-03-17 |  |  |  |  | Client : | [13 empty] | Doc.
Chd. | [20 empty] | Subject :
Date |  | 2025-03-17 |  |  |  |  | Contract No.- |  |  |  | https://www.flasysdesign.com/ | [13 empty] | Rev. No.
CALCULATIONS FOR CT & PT PARAMETERS IN ARAR GENERATION EXPANSION PROJECT
REFERENCE DATA
| 1) | Short Cicruit Study
2) General Site Layout -
3) SEC -EOA's Specification :
4) Main One line diagram(480V Swgr)
| 5) | 480V Aux One line Diagram
480V Switchgear Incomer CT sizing
1) Calculation of parameters for SAT Neutral side CT used for Earth Fault 51G protection.
BCT-HY.C1
|  | Station Auxiliary Transformer Rating | [12 empty] | = | 3 MVA , ONAN
4.16/0.480kV, Dyn11, Z=8% at ONAN rating
|  | Therefore full load currrent on 480V Side | [12 empty] | = | (MVAx 1000)/(1.732 x kV)
[15 empty] | = | 3 | x | 1000 |  | / | 1.732 | x | 0.48
[15 empty] | = | 3608.545 |  |  |  | Amps
|  | CT ratio chosen | [5 empty] | = | 4000/1 A
|  | Relay Used |  |  |  | : SPAJ110C
Knee Point Voltage Formulae
|  | The rated knee point voltage | [8 empty] | Ek | = | Kx (Rct+Rb) x Isn |  |  |  | ( IEC 60044-1 Amend, Page 17)
where
[6 empty] | Kx |  | = | Dimensioning facor
[6 empty] | Rct |  | = | Maximum resistance of secondary winding
[6 empty] | Isn |  | = | Rated secondary current
[6 empty] | Rb |  | = | Rated resistive burden
[8 empty] | = | Rrelay + 2Rl
[6 empty] | Rl |  | = | Cable resistance between CT & Relay
Knee Point Voltage calculation
|  | The actual fault as per short cirucit study is 45.7kA. Considering 20% margin it is | [19 empty] | 54.84 |  | KA
[6 empty] | Kx |  | = | 54.84/ 2000
[8 empty] | = | 27.42
[6 empty] | Rct |  | = | 14
[6 empty] | Rb |  | = | Rrelay + 2Rl
The CT burdens of numerical relays are below 0.1VA and can therefore be neglected
Considering 6 sq.mm copper conductor cable between CT and relay, resistance of
|  | 6 sq.mm copper cable | [7 empty] | = | 3.5 |  | Ohms / km
|  | Maximum cable length | [7 empty] | = | 50 |  | M |  | (from site plan)
|  | Cable Lead Resistance for the loop Rl = | [13 empty] | 2 | x | 3.5 |  | x | 0.05
[10 empty] | = | 0.35 |  | Ohms
[6 empty] | Rb |  |  |  | = | 0.35
|  | Knee point voltage Ek | [7 empty] | = | 27.42 | x | (14 + 0.35)
[10 empty] | = | 393.477
Considering a margin of 20% on Ek as per PTS-1022, Appendix-V, Page 20 of 46
[10 empty] | = | 472.1724
[8 empty] | Ek |  | = | 475 |  | V
[8 empty] | CT Class = |  |  |  | PX
Therefore CT chosen
[5 empty] | CT RATIO | [8 empty] | 4000/1 A
[5 empty] | Knee Point Voltage | [7 empty] | >= | 475 |  | V
[5 empty] | CT Wdg. Res. Rct | [7 empty] | = | 14 | ohms
[5 empty] | CT Class | [8 empty] | PX
[5 empty] | CT Cable to be used | [8 empty] | 6 sq.mm copper cable
2) Calculation of CT parameters for ( 51& 51N) on LV side of SAT
CT-101F.C1
CT Ratio Selection :
|  | SAT Rating | [11 empty] | = | 3 |  | MVA
|  | Full Load current on 0.48kV side | [11 empty] | = | (MVAx 1000)/(1.732 x kV)
[14 empty] | = | 3608.4392 |  | A
|  | CT ratio selected on 480V side is | [12 empty] | = | 4000 /1 Amp
Relay Used : SPAJ140C
Knee Point Voltage Formulae
|  | The rated knee point voltage | [8 empty] | Ek | = | Kx (Rct+Rb) x Isn |  |  |  | ( IEC 60044-1 Amend, Page 17)
where
[6 empty] | Kx |  | = | Dimensioning facor
[6 empty] | Rct |  | = | Maximum resistance of secondary winding
[6 empty] | Isn |  | = | Rated secondary current
[6 empty] | Rb |  | = | Rated resistive burden
[8 empty] | = | Rrelay + 2Rl
[6 empty] | Rl |  | = | Cable resistance between CT & Relay
Knee Point Voltage calculation
|  | The actual fault as per short cirucit study is 45.7KA. Considering 20% margin it is | [19 empty] | 54.84 |  | KA
[6 empty] | Kx |  | = | 54.84/ 2000
[8 empty] | = | 27.42
[6 empty] | Rct |  | = | 14
[6 empty] | Rb |  | = | Rrelay + 2Rl
The CT burdens of numerical relays are below 0.1VA and can therefore be neglected
Considering 6 sq.mm copper conductor cable between CT and relay, resistance of
|  | 6 sq.mm copper cable | [7 empty] | = | 3.5 |  | Ohms / km
|  | Maximum cable length | [7 empty] | = | 50 |  | M |  | (from site plan)
|  | Cable Lead Resistance for the loop Rl = | [13 empty] | 2 | x | 3.5 |  | x | 0.05
[10 empty] | = | 0.35 |  | Ohms
[6 empty] | Rb |  |  |  | = | 0.35
|  | Knee point voltage Ek | [7 empty] | = | 27.42 | x | (14 + 0.35)
[10 empty] | = | 393.477
Considering a margin of 20% on Ek as per PTS-1022, Appendix-V, Page 20 of 46
[10 empty] | = | 472.1724
[8 empty] | Ek |  | = | 475 |  | V
[8 empty] | CT Class = |  |  |  | PX
Therefore CT chosen
[5 empty] | CT RATIO | [8 empty] | 4000 /1 Amp
[5 empty] | Knee Point Voltage | [7 empty] | >= | 475 |  | V
[5 empty] | CT Wdg. Res. Rct | [7 empty] | = | 14 | ohms
[5 empty] | CT Class | [8 empty] | PX
[5 empty] | CT Cable to be used | [8 empty] | 6 sq.mm copper cable
3) SAT LV side metering CT
CT-101F.C1
|  | Meters | [11 empty] | 0.05 |  |  | As per ION metering catalogue
[10 empty] | Total |  |  |  | 0.05
|  | CT VA burden selected is | [9 empty] | 30VA
|  | Voltage developed across CT at rated current(1A) = | [13 empty] | 1 x (Rct + 30) |  |  | V
[14 empty] | = |  | 1 x (14 + 30)
[14 empty] | = | 44V
Isf selected is 5
|  | Therefore during fault voltage across CT = | [10 empty] | 5 x (Rct + 30) V
[13 empty] | = | 185 | V
When the connected burden is 0.05 the voltage developed is
[13 empty] | = | y x (14 + 0.05) |  |  |  | Where y is magnified Isf)
[12 empty] | y | = | 13.1673
|  | Therefore CT chosen | [13 empty] | 4000 /1 A.
30 VA
CL.0.5
ISF <5.
4) Calculation of parameters for 480V VT on LV side of SAT & Bus VT
| VT ratio chosen | [11 empty] | = | 480/ 3 /115/ 3
| VT will be with dual accuracy | [11 empty] | = | 0.5 / 3P class
| Equipment | [12 empty] | VA Burdens
| Meters | [12 empty] | 0.05 |  | As per ION catalogue
| 27-1 & 2 | [12 empty] | 0.5 |  | ABB catalogue
| Total | [12 empty] | 0.55
[5 empty] | Therefore PT chosen | [5 empty] | = | 480/ 3 /115/ 3 |  |  |  | V
0.5 / 3P class
100 VA
Unit Switchgear Incomer
5) Calculation of parameters for UAT Neutral side CT used for 51G protection.
BCT-HY.C1
Refer CT calculation for GT and UAT bay
6) Calculation of CT parameters for ( 50/51& 51N) on LV side of UAT & Incomer from Station Swgr
CT-201F.C1 & CT-202F.C1
|  | UAT Rating | [11 empty] | = | 1.25 |  | MVA
|  | Full Load current on 0.48kV side | [11 empty] | = | (MVAx 1000)/(1.732 x kV)
[14 empty] | = | 1503.5163 |  | A
|  | CT ratio selected on 480V side is | [12 empty] | = | 2000 /1 Amp
Knee Point Voltage Formulae
Knee Point Voltage Formulae
|  | The rated knee point voltage | [8 empty] | Ek | = | Kx (Rct+Rb) x Isn |  |  |  | ( IEC 60044-1 Amend, Page 17)
where
[6 empty] | Kx |  | = | Dimensioning facor
[6 empty] | Rct |  | = | Maximum resistance of secondary winding
[6 empty] | Isn |  | = | Rated secondary current
[6 empty] | Rb |  | = | Rated resistive burden
[8 empty] | = | Rrelay + 2Rl
[6 empty] | Rl |  | = | Cable resistance between CT & Relay
Knee Point Voltage calculation
|  |  |  | The actual fault as per short cirucit study is 44kA. Considering 20% margin it is | [17 empty] | 52.8 |  | KA
[6 empty] | Kx |  | = | 52.8/ 2000
[8 empty] | = | 26.4
[6 empty] | Rct |  | = | 7
[6 empty] | Rb |  | = | Rrelay + 2Rl
The CT burdens of numerical relays are below 0.1VA and can therefore be neglected
Considering 6 sq.mm copper conductor cable between CT and relay, resistance of
|  | 6 sq.mm copper cable | [7 empty] | = | 3.5 |  | Ohms / km
|  | Maximum cable length | [7 empty] | = | 50 |  | M |  | (from site plan)
|  | Cable Lead Resistance for the loop Rl = | [13 empty] | 2 | x | 3.5 |  | x | 0.05
[10 empty] | = | 0.35 |  | Ohms
[6 empty] | Rb |  |  |  | = | 0.35
|  | Knee point voltage Ek | [7 empty] | = | 26.4 | x | (7 + 0.35)
[10 empty] | = | 194.04
Considering a margin of 20% on Ek as per PTS-1022, Appendix-V, Page 20 of 46
[10 empty] | = | 232.848
[8 empty] | Ek |  | = | 250 |  | V
[8 empty] | CT Class = |  |  |  | PX
Therefore CT chosen
[5 empty] | CT RATIO | [8 empty] | 2000 /1 Amp
[5 empty] | Knee Point Voltage | [7 empty] | >= | 250 |  | V
[5 empty] | CT Wdg. Res. Rct | [7 empty] | = | 7 | ohms
[5 empty] | CT Class | [8 empty] | PX
[5 empty] | CT Cable to be used | [8 empty] | 6 sq.mm copper cable
| 7) | Calculation of parameters for UAT LV side Overall Unit Differential Protection 87OA.
CT-201F.C3
Refer CT calculation for GT and UAT bay
8) Calculation of parameters for 480V VT for Incomers & Bus VT
PT201
Refer Calculation for GT and UAT bay
9) Incomer metering CT
CT-201F.C2 & CT-202F.C2
Refer Calculation for GT and UAT bay
Station Switchgear & Unit Switchgear Outgoing feeders
10) 800A Feeder(Typ)- 50/51, 50N/51N
|  | CT ratio selected | [12 empty] | = | 800 /1 Amp
Knee Point Voltage Formulae
|  | The rated knee point voltage | [8 empty] | Ek | = | Kx (Rct+Rb) x Isn |  |  |  | ( IEC 60044-1 Amend, Page 17)
where
[6 empty] | Kx |  | = | Dimensioning facor
[6 empty] | Rct |  | = | Maximum resistance of secondary winding
[6 empty] | Isn |  | = | Rated secondary current
[6 empty] | Rb |  | = | Rated resistive burden
[8 empty] | = | Rrelay + 2Rl
[6 empty] | Rl |  | = | Cable resistance between CT & Relay
Knee Point Voltage calculation
[6 empty] | Kx |  | = | 20
[6 empty] | Rct |  | = | 3
[6 empty] | Rb |  | = | Rrelay + 2Rl
The CT burdens of numerical relays are below 0.1VA and can therefore be neglected
Rl is neglible as they are internally wired.
|  | Knee point voltage Ek | [7 empty] | = | 20 | x | 3
[10 empty] | = | 60
Considering a margin of 20% on Ek as per PTS-1022, Appendix-V, Page 20 of 46
[10 empty] | = | 72
[8 empty] | Ek |  | = | 100 |  | V
[8 empty] | CT Class = |  |  |  | PX
Therefore CT chosen
[5 empty] | CT RATIO | [8 empty] | 800 /1 Amp
[5 empty] | Knee Point Voltage | [7 empty] | >= | 100 |  | V
[5 empty] | CT Wdg. Res. Rct | [7 empty] | = | 3 | ohms
[5 empty] | CT Class | [8 empty] | PX
11) 1000A Feeder(Typ)- 50/51, 50N/51N
|  | CT ratio selected | [12 empty] | = | 1000 /1 Amp
Knee Point Voltage Formulae
|  | The rated knee point voltage | [8 empty] | Ek | = | Kx (Rct+Rb) x Isn |  |  |  | ( IEC 60044-1 Amend, Page 17)
where
[6 empty] | Kx |  | = | Dimensioning facor
[6 empty] | Rct |  | = | Maximum resistance of secondary winding
[6 empty] | Isn |  | = | Rated secondary current
[6 empty] | Rb |  | = | Rated resistive burden
[8 empty] | = | Rrelay + 2Rl
[6 empty] | Rl |  | = | Cable resistance between CT & Relay
Knee Point Voltage calculation
[6 empty] | Kx |  | = | 20
[6 empty] | Rct |  | = | 3.5
[6 empty] | Rb |  | = | Rrelay + 2Rl
The CT burdens of numerical relays are below 0.1VA and can therefore be neglected
Rl is neglible as they are internally wired.
|  | Knee point voltage Ek | [7 empty] | = | 20 | x | 3.5
[10 empty] | = | 70
Considering a margin of 20% on Ek as per PTS-1022, Appendix-V, Page 20 of 46
[10 empty] | = | 84
[8 empty] | Ek |  | = | 100 |  | V
[8 empty] | CT Class = |  |  |  | PX
Therefore CT chosen
[5 empty] | CT RATIO | [8 empty] | 1000 /1 Amp
[5 empty] | Knee Point Voltage | [7 empty] | >= | 100 |  | V
[5 empty] | CT Wdg. Res. Rct | [7 empty] | = | 3.5 | ohms
[5 empty] | CT Class | [8 empty] | PX
12) 2000A Feeder(Typ)- 50/51, 50N/51N
|  | CT ratio selected | [12 empty] | = | 2000 /1 Amp
Knee Point Voltage Formulae
|  | The rated knee point voltage | [8 empty] | Ek | = | Kx (Rct+Rb) x Isn |  |  |  | ( IEC 60044-1 Amend, Page 17)
where
[6 empty] | Kx |  | = | Dimensioning facor
[6 empty] | Rct |  | = | Maximum resistance of secondary winding
[6 empty] | Isn |  | = | Rated secondary current
[6 empty] | Rb |  | = | Rated resistive burden
[8 empty] | = | Rrelay + 2Rl
[6 empty] | Rl |  | = | Cable resistance between CT & Relay
Knee Point Voltage calculation
[6 empty] | Kx |  | = | 20
[6 empty] | Rct |  | = | 7
[6 empty] | Rb |  | = | Rrelay + 2Rl
The CT burdens of numerical relays are below 0.1VA and can therefore be neglected
Rl is neglible as they are internally wired.
|  | Knee point voltage Ek | [7 empty] | = | 20 | x | 7
[10 empty] | = | 140
Considering a margin of 20% on Ek as per PTS-1022, Appendix-V, Page 20 of 46
[10 empty] | = | 168
[8 empty] | Ek |  | = | 175 |  | V
[8 empty] | CT Class = |  |  |  | PX
Therefore CT chosen
[5 empty] | CT RATIO | [8 empty] | 2000 /1 Amp
[5 empty] | Knee Point Voltage | [7 empty] | >= | 175 |  | V
[5 empty] | CT Wdg. Res. Rct | [7 empty] | = | 7 | ohms
[5 empty] | CT Class | [8 empty] | PX
13 ) CT parameters for Station switchgear Bus coupler protection , 51
CT1.1
|  | CT ratio selected | [12 empty] | = | 4000 /1 Amp
Knee Point Voltage Formulae
|  | The rated knee point voltage | [8 empty] | Ek | = | Kx (Rct+Rb) x Isn |  |  |  | ( IEC 60044-1 Amend, Page 17)
where
[6 empty] | Kx |  | = | Dimensioning facor
[6 empty] | Rct |  | = | Maximum resistance of secondary winding
[6 empty] | Isn |  | = | Rated secondary current
[6 empty] | Rb |  | = | Rated resistive burden
[8 empty] | = | Rrelay + 2Rl
[6 empty] | Rl |  | = | Cable resistance between CT & Relay
Knee Point Voltage calculation
[6 empty] | Kx |  | = | 20
[6 empty] | Rct |  | = | 14
[6 empty] | Rb |  | = | Rrelay + 2Rl
The CT burdens of numerical relays are below 0.1VA and can therefore be neglected
Rl is neglible as they are internally wired.
|  | Knee point voltage Ek | [7 empty] | = | 20 | x | 14
[10 empty] | = | 280
Considering a margin of 20% on Ek as per PTS-1022, Appendix-V, Page 20 of 46
[10 empty] | = | 336
[8 empty] | Ek |  | = | 350 |  | V
[8 empty] | CT Class = |  |  |  | PX
Therefore CT chosen
[5 empty] | CT RATIO | [8 empty] | 4000 /1 Amp
[5 empty] | Knee Point Voltage | [7 empty] | >= | 350 |  | V
[5 empty] | CT Wdg. Res. Rct | [7 empty] | = | 14 | ohms
[5 empty] | CT Class | [8 empty] | PX