## CT & VA BURDEN
|  |  | CT & PT SIZING CALCULATION | [5 empty] | Ref.No.
[9 empty] | Revision |  | https://www.flasysdesign.com/
[9 empty] | Date |  | Email: contact@flasysdesign.com
Client
Consultant
Project |  |  | 10 MW POWER PLANT
SYSTEM DETAILS
| Generator Rating |  | 10.5 MW | Generator PF |  | 0.8
| Generator Voltage |  | : 11 KV | Generator FLC |  | : KW | 10500 | = | 10500 | 688.9041
[6 empty] | Ö3VCosF | (1.732*11*0.8) |  | 15.2416
| Generator FLC |  |  |  |  | 688.9041 | Amps
| After 25% of Over current |  |  |  |  | 861.1301 | Amps
Hence the Selected CT ratio will be 1000/1-1 Amps.
References :
1. Secure Meter Catalogue
2. MICOM Relay manual
1. TIE CB -1 TG Bulding Metering
| Sl. | Description |  |  | PT Circuit (PT1: Core-1) Metering core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA
| 1 | Ammeter |  |  | - | - | -
| 2 | Voltmeter |  |  | 1.5 | 1 | 1.5
| 3 | Digital Frequency Meter |  |  | 1 | 1 | 1
| 4 | Digital TVM Meter |  |  | 2 | 1 | 2
5
6
7
| 8 | Double Voltmeter |  |  | 2 | 1 | 2
| 9 | Double Frequency Meter |  |  | 2 | 1 | 2
| 10 | [5 empty] | 0
| 14 | [5 empty] | 0
| 15 | Synchroscope |  |  | 3 | 1 | 3
| 16 | Autosynchroniser |  |  | 0.2 | 1 | 0.2
| 17 | Check Synchronising Relay |  |  | 2.5 | 1 | 2.5
| 18 | No Volt Relays |  |  | 3 | 2 | 6
| 19 | PT Fuse failure |  |  | 11 | 1 | 11
| 20 | PQM Meter |  |  | 2 | 1 | 2
|  | Total Burden |  |  |  |  | 33.2
2. AVR Panel
| Sl. | Description |  |  | CT Circuit (CT 6.1-6.3) Metering Core |  |  | PT Circuit (PT2: Core-1)
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA | Burden in VA | Qty | Total Burden in VA
| 1 | Voltmeter |  |  | - | - | - | 2 | 1 | 2
| 2 | PF Meter |  |  | 1 | 1 | 1 | 1 | 1 | 1
| 3 | AVR Droop Ckt. |  |  | 5 | 2 | 10 | - | - | -
| 4 | AVR Cards |  |  | - | - | - | 10 | 2 | 20
|  | Total Burden |  |  |  |  | 11 |  |  | 23
3. Generator Relay Panel (GRP)
3.1 Generator Protection Relay(GPR-1 & GPR-2)
| Sl. | Description |  |  | CT Circuit (CT 7.1-.3) Protection core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA
| 1 | Multifunction relay(G60-1) |  |  | 0.2 | 1 | 0.2
|  | Total Burden |  |  |  |  | 0.2
| Sl. | Description |  |  | CT Circuit (CT 8.1-3 ) Protection core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA
| 1 | Multifunction relay(G60-2) |  |  | 0.2 | 1 | 0.2
|  | Total Burden |  |  |  |  | 0.2
| Sl. | Description |  |  | CT Circuit (CT 4.1-3) Protection core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA
| 1 | Multifunction relay(G60-2) |  |  | 0.2 | 1 | 0.2
|  | Total Burden |  |  |  |  | 0.2
| Sl. | Description |  |  | CT Circuit (CT 5.1-3 ) Protection core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA
| 1 | Multifunction relay(G60-1) |  |  | 0.2 | 1 | 0.2
|  | Total Burden |  |  |  |  | 0.2
| Sl. | Description |  |  | CT Circuit (CT 2) Protection core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA
| 1 | Multifunction relay(G60-2) |  |  | 0.2 | 1 | 0.2
|  | Total Burden |  |  |  |  | 0.2
| Sl. | Description |  |  | CT Circuit (CT 3 ) Protection core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA
| 1 | Multifunction relay(G60-1) |  |  | 0.2 | 1 | 0.2
|  | Total Burden |  |  |  |  | 0.2
| Sl. | Description |  |  | PT Circuit (PT1 : Core-2) Protection Core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA
| 1 | Multifunctional Relay (G60-1) |  |  | 0.25 | 1 | 0.25
|  | Total Burden |  |  |  |  | 0.25
| Sl. | Description |  |  | PT Circuit (PT2 : Core-2) Protection Core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA
| 1 | Multifunctional Relay(G60-2) |  |  | 0.25 | 1 | 0.25
| 2 | Directional Earthfault Relay(67N) |  |  | 2 | 1 | 2
|  | Total Burden |  |  |  |  | 2.25
3.2. Directional Earth fault Relay(67N)
| Sl. | Description |  |  | CT Circuit (CBCT-1) Protection core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA
| 1 | Directional Earthfault Relay(67N) |  |  | 2 | 1 | 2
|  | Total Burden |  |  |  |  | 2
3.3.Restricted Earth Fault (64R)
| Sl. | Description |  |  | CT Circuit (CBCT-2) Protection core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA
| 1 | Restricted Earth fault Relay(64R) |  |  | 3 | 1 | 3
|  | Total Burden |  |  |  |  | 3
| Sl. | Description |  |  | CT Circuit (CT 1) Protection core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA
| 1 | Restricted Earth fault Relay(64R) |  |  | 3 | 1 | 3
|  | Total Burden |  |  |  |  | 3
4. Tri Vector meter (TVM)
| Sl. | Description |  |  | CT Circuit (CT 9.1-3 ) metering core |  |  | PT circuit (PT3:core-1 )metering core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA | Burden in VA | Qty | Total Burden in VA
| 1 | Tri Vector Meter |  |  | 1 | 1 | 1 | 1.5 | 1 | 1.5
|  | Total Burden |  |  |  |  | 1 |  |  | 1.5
5. Tri Vector meter (TVM) - 3.3kV SWITCHBOARD
| Sl. | Description |  |  | CT-2,3,4&5 metering core |  |  | PT circuit (BPT:core-1 )metering core
| No. |  |  |  | Burden in VA | Qty | Total Burden in VA | Burden in VA | Qty | Total Burden in VA
| 1 | Tri Vector Meter |  |  | 1 | 1 | 1 | 1.5 | 5 | 7.5
|  | Total Burden |  |  |  |  | 1 |  |  | 7.5
| CT BURDEN |  |  |  |  | CAL. BURDEN | SELECTED BURDEN
| Total Burden on Phase side CT-1 ((64R) |  |  |  |  | 3VA | 20VA,CL: 5P20
| Total Burden on CT 2 (MICOM P343-2) |  |  |  |  | :0.2 VA | 20VA,CL: 5P20
| Total Burden on CT 3 (MICOM P343-1) |  |  |  |  | :0.2 VA | 20VA,CL: 5P20
| Total Burden on Phase side CT 6.1-6.3(AVR) |  |  |  |  | :11 VA | 20VA,CL: 0.2
| Total Burden on Phase side CT 7.1-3 (G60-2) |  |  |  |  | :0.2 VA | PS CLASS
| Total Burden on Phase side CT 8.1-3 (G60-1) |  |  |  |  | :0.2 VA | PS CLASS
| Total Burden on Phase side CT 9.1-3 (TVM) |  |  |  |  | :1VA | 10VA CL: 0.2
| Total Burden on Phase side CBCT-1(67N) |  |  |  |  | :2 VA | 20VA CL: 5P20
| Total Burden on Phase side CBCT-2 (64R) |  |  |  |  | :3VA | 20VA CL: 5P20
| PT BURDEN |  |  |  |  | CAL. BURDEN | SELECTED BURDEN
| Total Burden on PT1: Core-1 ( Metering Core) |  |  |  |  | :48.2VA | 50VA, CL. 0.2
| Total Burden on PT1: Core-2 ( Protection core-G60-1) |  |  |  |  | :0.25VA | 50VA, CL. 3P
| Total Burden on PT2: Core-1 (AVR)( Metering Core) |  |  |  |  | :23VA | 50VA, CL. 0.2
| Total Burden on PT2: Core-2 ( Protection-G60-2) |  |  |  |  | :2.25VA | 50VA, CL. 3P
| Total Burden on PT3: Core-1 (TVM)(Metering Core) |  |  |  |  | :1.5VA | 50VA, CL. 0.2
| Total Burden on PT3: Core-2 Spare |  |  |  |  | - | 50VA, CL. 0.2

## KNEE POINT VOLTAGE
|  | KNEE POINT VOLTAGE CALCULATION | [8 empty] | Ref.No.
[11 empty] | Revision | https://www.flasysdesign.com/
[11 empty] | Date | Email: contact@flasysdesign.com
User
Consultant
Project |  |  | 1X10.5 MW POWER PLANT.
SYSTEM DETAILS
| Generator Rating |  |  |  | : | 10.5 | MW
| Generator Voltage |  |  |  | : | 11 | KV
| Generator PF |  |  |  | : | 0.8
| Generator FLC |  |  |  | : | 688.9041 | Amps
| Sub transient reactance |  |  | Xd" | : | 19.1 | % | 0.191 | p.u. | (Assumed)
| CT winding resistance |  |  | Rct | : | 4 | Ohms
| Primary CT current |  |  |  | : | 1000 | Amps
| Secondary CT current |  |  |  | : | 1 | Amps
| Resistance of conn. Leads or Cable resistance |  |  | RL | : | 0.87 | ohms | considered 100M | 8.7 Ohms/KM
| Internal resistance of Relay |  |  | Rp | : | 0.2 | ohms
| CT Knee point voltage primary side |  |  |  | Vkp = | 2*If*.(Rct+RL+Rp)
|  |  |  | If | = | 40000 | A
[5 empty] | = | 40 | kA | (System fault level)
|  |  |  | If(sec) | = | If(pri)/CT ratio
[5 empty] | = | 40 | Amps
| CT Knee point voltage |  |  | Vkp | = | 2*If*.(Rct+RL+Rp)
[5 empty] | = | 405.6 | Volts
Selected Vkp = 250V. Hence safe.