## Cable Tray Size
https://www.flasysdesign.com/
Cable Tray Size Calculation: | [6 empty] | Email: contact@flasysdesign.com
| CABLE TRAY: FROM | A |  | TO | B |  | LENGTH OF CABLE TRAY (Meter): |  | 50
Sr. No. | Cable Route (From-To) | Type & Cable Size | Size of Cable (mm2) | No. of Cable | Overall Diameter of each Cable (mm) | Sum of Cable OD (mm) | Self Weight of Cable (Kg/Mt) | Total Weight of Cable (Kg/Mt) | Remarks
1 | T/C To D.G Panel-1 | 3.5C x 70 Sq. mm | 70 | 0 | 39.8 | 0 | 7.4 | 0
2 | T/C To D.G Panel-2 | 3.5C x 300 Sq. mm | 35 | 1 | 30.6 | 30.6 | 7.4 | 7.4
3 | T/C To D.G Panel-3 | 3.5C x 300 Sq. mm | 25 | 3 | 30 | 90 | 7.4 | 22.2
4 | T/C To LT Panel-1 | 3.5C x 300 Sq. mm |  |  |  | 0 |  | 0
5 | T/C To LT Panel-2 | 3.5C x 300 Sq. mm |  |  |  | 0 |  | 0
6 | T/C To LT Panel-3 | 3.5C x 400 Sq. mm |  |  |  | 0 |  | 0
7 | [5 empty] | 0 |  | 0
8 | [5 empty] | 0 |  | 0
9 | [5 empty] | 0 |  | 0
10 | [5 empty] | 0 |  | 0
11 | [5 empty] | 0 |  | 0
12 | [5 empty] | 0 |  | 0
13 | [5 empty] | 0 |  | 0
14 | [5 empty] | 0 |  | 0
15 | [5 empty] | 0 |  | 0
Total |  |  |  | 4 |  | 120.6 | 22.2 | 29.6
:Calculation: | [5 empty] | :Result:
Maximum Cable Diameter: |  |  | 39.8 | mm |  | Selected Cable Tray width: |  | O.K
Consider Spare Capacity of Cable Tray: |  |  | 40% |  |  | Selected Cable Tray Depth: |  | O.K
Distance between each Cable: |  |  | 10 | mm |  | Selectrd Cable Tray Weight: |  | O.K | Including Spare Capacity | 1
Calculated Width of Cable Tray: |  |  | 224.84 | mm |  | Selected Cable Tray Size: |  | O.K |  | 160.6
Calculated Area of Cable Tray: |  |  | 8948.632 | Sq.mm | [5 empty] | 6391.88
No of Layer of Cables in Cable Tray: |  |  | 1 |  |  | Required Cable Tray Size: |  | 250X50 | mm | 1
Selected No of Cable Tray: |  |  | 1 | No |  | Required Nos of Cable Tray: |  | 1 | No
Selected Cable Tray Width: |  |  | 250 | mm |  | Required Cable Tray Weight: |  | 120 | Kg/Meter/Tray
Selected Cable Tray Depth: |  |  | 50 | mm |  | Type of Cable Tray: |  | Perforated |  | 250
Selected Cable Tray Weight Capacity: |  |  | 120 | Kg/Meter |  | Total Length of Cable Tray: |  | 50 | Meter | 12500
Type of Cable Tray: |  |  | Perforated |  |  | Cable Tray Width Area Remaning: |  | 10.06%
Total Area of Cable Tray: |  |  | 12500 | Sq.mm |  | Cable Tray Area Remaning: |  | 28.41%
Standard Ladder Type Cable Tray |  |  | Width | 150/200/300/450/600 mm
|  |  | Height | 50/75/100 mm
Standard Perforated Type Cable Tray |  |  | Width | 150/200/300/450/600 mm
|  |  | Height | 25/50 mm