## L SIDE
LUNAR ELECTRO
CABLE TRAY SIZE CALCULATION
Cable Tray size at LV Room to B1 Electrical Room
https://www.flasysdesign.com/
Email: contact@flasysdesign.com
SR. NO | Cable size in Sq. mm | Cable OD in mm | No. of cables | Total width of cables in mm | Size of ECC in mm | Dia of ECC in mm | Width of ECC in mm
1 | 4c x 6 | 19 |  | 0 | 6 | 5.2 | 0
2 | 4c x 10 | 21 |  | 0 | 10 | 6.7 | 0
3 | 4c x 16 | 24 |  | 0 | 16 | 7.8 | 0
4 | 4c x 25 | 29 |  | 0 | 16 | 7.8 | 0
5 | 4c x 35 | 29 |  | 0 | 16 | 7.8 | 0
6 | 4c x 50 | 33 |  | 0 | 25 | 9.7 | 0
7 | 4c x 70 | 39 |  | 0 | 35 | 10.9 | 0
8 | 4c x 95 | 42 | 4 | 168 | 50 | 12.8 | 51.2
10 | 4c x 120 | 47 | 4 | 188 | 70 | 14.6 | 58.4
11 | 4c x 150 | 52 |  | 0 | 95 | 17.1 | 0
12 | 4c x 185 | 57 |  | 0 | 95 | 17.1 | 0
13 | 4c x 240 | 63 |  | 0 | 120 | 18.8 | 0
14 | 4c x 300 | 69 |  | 0 | 150 | 20.9 | 0
15 | 2c x 25 | 24 | 2 | 48 | 16 | 7.8 | 15.6
|  | Total No of Cables | 10 | 404 |  |  | 125.2
|  |  |  | Actual width of cable tray |  |  | 933.2
|  |  |  | Required Cable Tray Size keeping 30% space |  |  | 1333.1428
|  |  |  | Selected Cable Tray Size in mm |  | 600+600+600=1800
For 1500kVA Transformer | 1c x 630 | 49 | 11 | 539 |  | Standard Cable Tray Sizes
| 1c x 150 | 22.5 | 2 | 45 |  | 100 mm
| Actual width of cable tray |  |  | 584 |  | 150 mm
| Required Cable Tray Size keeping 30% space |  |  | 1168 |  | 200 mm
| Selected Cable Tray Size in mm |  |  | 600 + 300 |  | 300 mm
For 1000kVA Transformer | 1c x 630 | 49 | 7 | 343 |  | 400 mm
450 mm
| 1c x 150 | 22.5 | 2 | 45 |  | 500 mm
| Actual width of cable tray |  |  | 388 |  | 600 mm
| Required Cable Tray Size keeping 40% space |  |  | 659.6
| Selected Cable Tray Size in mm |  |  | 600 + 200
Type of Cable : Cu / XLPE / SWA / PVC - 0.6 / 1KV
Type of Cable : Cu / XLPE / AWA / PVC - 0.6 / 1KV

## R SIDE
LUNAR ELECTRO
CABLE TRAY SIZE CALCULATION
Cable Tray size at LV Room to B1 Electrical Room
https://www.flasysdesign.com/
Email: contact@flasysdesign.com
SR. NO | Cable size in Sq. mm | Cable OD in mm | No. of cables | Total width of cables in mm | Size of ECC in mm | Dia of ECC in mm | Width of ECC in mm
1 | 4c x 6 | 19 |  | 0 | 6 | 5.2 | 0
2 | 4c x 10 | 21 |  | 0 | 10 | 6.7 | 0
3 | 4c x 16 | 24 |  | 0 | 16 | 7.8 | 0
4 | 4c x 25 | 29 |  | 0 | 16 | 7.8 | 0
5 | 4c x 35 | 29 |  | 0 | 16 | 7.8 | 0
6 | 4c x 50 | 33 |  | 0 | 25 | 9.7 | 0
7 | 4c x 70 | 39 |  | 0 | 35 | 10.9 | 0
8 | 4c x 95 | 42 |  | 0 | 50 | 12.8 | 0
10 | 4c x 120 | 47 |  | 0 | 70 | 14.6 | 0
11 | 4c x 150 | 52 |  | 0 | 95 | 17.1 | 0
12 | 4c x 185 | 57 |  | 0 | 95 | 17.1 | 0
13 | 4c x 240 | 63 |  | 0 | 120 | 18.8 | 0
14 | 4c x 300 | 69 |  | 0 | 150 | 20.9 | 0
15 | 2c x 25 | 24 |  | 0 | 16 | 7.8 | 0
|  | Total No of Cables | 0 | 0 |  |  | 0
|  |  |  | Actual width of cable tray |  |  | 0
|  |  |  | Required Cable Tray Size keeping 30% space |  |  | 0
|  |  |  | Selected Cable Tray Size in mm |  | 600+600+600=1800
For 1500kVA Transformer | 1c x 630 | 49 | 11 | 539 |  | Standard Cable Tray Sizes
| 1c x 150 | 22.5 | 2 | 45 |  | 100 mm
| Actual width of cable tray |  |  | 584 |  | 150 mm
| Required Cable Tray Size keeping 30% space |  |  | 1168 |  | 200 mm
| Selected Cable Tray Size in mm |  |  | 600 + 300 |  | 300 mm
For 1000kVA Transformer | 1c x 630 | 49 | 7 | 343 |  | 400 mm
450 mm
| 1c x 150 | 22.5 | 2 | 45 |  | 500 mm
| Actual width of cable tray |  |  | 388 |  | 600 mm
| Required Cable Tray Size keeping 40% space |  |  | 659.6
| Selected Cable Tray Size in mm |  |  | 600 + 200
Type of Cable : Cu / XLPE / SWA / PVC - 0.6 / 1KV
Type of Cable : Cu / XLPE / AWA / PVC - 0.6 / 1KV

## flasys
LUNAR ELECTRO
CABLE TRAY SIZE CALCULATION
Cable Tray size at LV Room to B1 Electrical Room
[5 empty] | https://www.flasysdesign.com/ |  |  | https://www.flasysdesign.com/
[5 empty] | Email: contact@flasysdesign.com |  |  | Email: contact@flasysdesign.com
SR. NO | Cable size in Sq. mm | Cable OD in mm | No. of cables | Total width of cables in mm | Size of ECC in mm | Dia of ECC in mm | Width of ECC in mm
1 | 4c x 6 | 19 |  | 0 | 6 | 5.2 | 0
2 | 4c x 10 | 21 | 1 | 21 | 10 | 6.7 | 6.7
3 | 4c x 16 | 24 |  | 0 | 16 | 7.8 | 0
4 | 4c x 25 | 29 | 1 | 29 | 16 | 7.8 | 7.8 |  |  | S
5 | 4c x 35 | 29 |  | 0 | 16 | 7.8 | 0
6 | 4c x 50 | 33 |  | 0 | 25 | 9.7 | 0
7 | 4c x 70 | 39 | 1 | 39 | 35 | 10.9 | 10.9
8 | 4c x 95 | 42 |  | 0 | 50 | 12.8 | 0
10 | 4c x 120 | 47 |  | 0 | 70 | 14.6 | 0 |  | K&A | NORR
11 | 4c x 150 | 52 |  | 0 | 95 | 17.1 | 0 |  | 25% | 30%
12 | 4c x 185 | 57 | 2 | 114 | 95 | 17.1 | 34.2 |  | 538.75 | 560.3
13 | 4c x 240 | 63 |  | 0 | 120 | 18.8 | 0
14 | 4c x 300 | 69 |  | 0 | 150 | 20.9 | 0 |  | DIFF | 21.55 | mm
|  | Total No of Cables | 5 | 203 |  |  | 59.6
406
| Enter one bigger cable Dia. |  | 25 |  |  |  | 25
| Cable tray width |  | 431