## Earthing Calculation
EARTHING CALCULATION
Project name: |  | 400.4kWp
Client Name:
Resistance of Earth electrode as per BS 7430
Considering Maintenance free Earth Pit with bore dia 17.2 mm and 3 mtr long
| R = | 1/2πL [ (ρ - ρc) (loge[8L/D] - 1) + ρc (loge[8L/d] - 1) ]
Where,
rc = | Resistivity of the infill material in ohm-m = |  |  |  | 0.2 | ohm-m
D = | Diameter of the infill material in m = |  |  |  | 0.1 | m
l = | Length of the rod or pipe in m = |  |  |  | 3 | m
d = | Diameter of the rod in m = |  |  |  | 0.017 | m
r = | Resistivity of the soil in (ohm-m) = |  |  |  | 6.34 | ohm-m
|  |  | R = | 1.5266 | ohm
Total electrodes considered for individual AC or DC Earthing = 2 Nos
Effective resistance of electrode (Re) expressed as : |  |  |  |  | 1/Re = 1/R1 + 1/R2
|  |  |  | Re = | ( R1 x R2)/( R1 + R2 )
|  |  |  | = | (1.53x1.53)/(1.53+1.53)
|  |  |  | Re = | 0.765 ohm
SOLAR ARRAY AREA EARTH GRID
Resistance of Earth strip as per IS: 3043 (9.2.3)
DC Side
length of earth strip (25X3mm, GI) is buried in the plant at 100mm depth | [5 empty] | 160 | Meter
|  |  | R = | (100ρ/2πl) loge(2l²/wt)
Where,
| r = | Resistivity of the soil ( ohm-Meter) |  |  | 6.34 | ohm-m
| l = | Length of the strip in cm |  |  | 16000 | cm
| w = | Depth of the burial cm |  |  | 0.3 | cm
| t = | Width of the strip |  |  | 2.5 | cm
|  |  | R = | 0.12835 | ohm
Total Effective Resistance of the System = |  |  |  | Strip Resistance + Effective Resistance of Pit
|  |  | RTotal = | 0.895 ohm
Therefore, According to the Tender Value the Resistance of the Should be smaller than 4 ohm.
AC Side
length of earth strip (25X3mm, GI) is buried in the plant at 100mm depth | [5 empty] | 175 | Meter
|  |  | R = | (100ρ/2πl) loge(2l²/wt)
Where,
| r = | Resistivity of the soil ( ohm-Meter) |  |  | 6.34 | ohm-m
| l = | Length of the strip in cm |  |  | 17500 | cm
| w = | Depth of the burial cm |  |  | 0.3 | cm
| t = | Width of the strip |  |  | 2.5 | cm
|  |  | R = | 0.11838 | ohm
Total Effective Resistance of the System = |  |  |  | Strip Resistance + Effective Resistance of Pit
|  |  | RTotal = | 0.885 ohm
Therefore, According to the Tender Value the Resistance of the Should be smaller than 4 ohm.

## EARTH STRIP SIZE CALCULATION
EARTH STRIP SIZE CALCULATION
Project name: |  | 400.4kWp
Client Name:
EARTH STRIP CALCULATION
AS PER IS: 3043
| K = | √ ( (Qc (B+20))/δ20) ) ln ( 1+ ( θt-θ1)/(B+θ1) )
Where,
Qc = | Volumetric heat capacity of conductor material ( j/°C mm3)
B = | Reciprocal of temperature coefficient of resistivity at 0°C for the conductor (°C)
δ20 = | Electrical resistivity of conductor material at 20°C (ohm-mm)
θ1 = | Initial temperature of conductor = |  |  |  |  | 50
θt = | Final temperature of Steel conductor = |  |  |  |  | 500
Material constants as per IS-3043-1987 Table-5
|  |  | Steel | Aluminium | Copper
|  | B | 202 | 228 | 234.5
|  | Qc | 0.0038 | 0.0025 | 0.00345
|  | δ20 | 0.000138 | 2.8264e-05 | 1.7241e-05
For GI Strip
| K = | √ ( ( 0.0038 (202 + 20) )/0.000138) ) ln ( 1+ (500-50)/(202 + 50) )
|  |  | K = | 79.1381
DC Side
| No. Of Parallel Strings at Inverters |  |  |  | 80 | Nos
| Current Per String |  |  |  | 9.14 | A
| Total Fault Current at Sixteen Inverters (If) |  |  |  | 731.2 | A
| Safety Factor (125 %) |  |  |  | 914 | A
| Corrosion Effect (1 % Every for 25 years) |  |  |  | 1142.5 | A
Area of Cross Section (A) = Fault Current (If) X Fault Current Time √(t)/ Material Constant (K)
| Area of Cross Section (A) = |  |  | 14.4368 | Sqmm
Where,
| If = | Fault Current |  | 1142.5 | Ampere
| t = | Fault Current time |  | 1 | Second
| K = | Material Constant |  | 79.1381
Earth Strip Size Selected |  |  |  | 25 X 3 | Sqmm
AC Side
In case of AC System the fault current produced due to the Solar Inverters and the source of
supply from grid side, which is supplied by the transformer of 1000kVA already installed at IOCL
site.
Fault current is given by:
|  |  | If = | S
√3 X U X % Z
|  |  | If = | 1000kVA
√3 X 415V X 0.05
|  |  | If = | 27824.9256 | Ampere
Where,
|  |  | Ir = | Rated Current
|  |  | S = | Rated Power (1000kVA)
|  |  | U = | Rated Voltage (415 V)
|  |  | %Z = | Percent Impedence (5% as per IS 2026 (Part 1))
Fault Current produced by the Inverters:
| No. Of Parallel Inverters (25kW) at ACCB |  |  |  | 16 | Nos
| Current Per Inverter |  |  |  | 36.2 | A
| Total Fault Current at Sixteen Inverters (If) |  |  |  | 724 | A
| Safety Factor (125 %) |  |  |  | 905 | A
| Corrosion Effect (1 % Every for 25 years) |  |  |  | 1131.25 | A
Area of Cross Section (A) = Fault Current (If) X Fault Current Time √(t)/ Material Constant (K)
| Area of Cross Section (A) = |  |  | 365.8942 | Sqmm
Where,
| If = | Fault Current (PV Side + Grid Side) |  |  | 28956.1756 | Ampere
| t = | Fault Current time |  |  | 1 | Second
| K = | Material Constant |  |  | 79.1381
At AC Side the equipments will be connected by two 50x6 Strips by end to end.
Total cross section area of the strips is 600 Sqmm which is greater than the above required cross section.
Earth Strip Size Selected |  |  |  | 50X6 | Sqmm

## EARTH STRIP SIZE CALCULATIO (2)
EARTH STRIP SIZE CALCULATION
Project name: |  | 400.4kWp
Client Name:
EARTH STRIP CALCULATION
AS PER IS: 3043
| K = | √ ( (Qc (B+20))/δ20) ) ln ( 1+ ( θt-θ1)/(B+θ1) )
Where,
Qc = | Volumetric heat capacity of conductor material ( j/°C mm3)
B = | Reciprocal of temperature coefficient of resistivity at 0°C for the conductor (°C)
δ20 = | Electrical resistivity of conductor material at 20°C (ohm-mm)
θ1 = | Initial temperature of conductor = |  |  |  |  | 50
θt = | Final temperature of Steel conductor = |  |  |  |  | 500
Material constants as per IS-3043-1987 Table-5
|  |  | Steel | Aluminium | Copper
|  | B | 202 | 228 | 234.5
|  | Qc | 0.0038 | 0.0025 | 0.00345
|  | δ20 | 0.000138 | 2.8264e-05 | 1.7241e-05
For GI Strip
| K = | √ ( ( 0.0038 (202 + 20) )/0.000138) ) ln ( 1+ (500-50)/(202 + 50) )
|  |  | K = | 79.1381
DC Side
| No. Of Parallel Strings at Inverters |  |  |  | 80 | Nos
| Current Per String |  |  |  | 9.14 | A
| Total Fault Current at Sixteen Inverters (If) |  |  |  | 731.2 | A
| Safety Factor (125 %) |  |  |  | 914 | A
| Corrosion Effect (1 % Every for 25 years) |  |  |  | 1142.5 | A
Area of Cross Section (A) = Fault Current (If) X Fault Current Time √(t)/ Material Constant (K)
| Area of Cross Section (A) = |  |  | 14.4368 | Sqmm
Where,
| If = | Fault Current |  | 1142.5 | Ampere
| t = | Fault Current time |  | 1 | Second
| K = | Material Constant |  | 79.1381
Earth Strip Size Selected |  |  |  | 25 X 3 | Sqmm
AC Side
In case of AC System the fault current produced due to the Solar Inverters and the source of
supply from grid side, which is supplied by the transformer of 1000kVA already installed at IOCL
site.
Fault current is given by:
|  |  | If = | S
√3 X U X % Z
|  |  | If = | 1000kVA
√3 X 415V X 0.05
|  |  | If = | 27824.9256 | Ampere
Where,
|  |  | Ir = | Rated Current
|  |  | S = | Rated Power (1000kVA)
|  |  | U = | Rated Voltage (415 V)
|  |  | %Z = | Percent Impedence (5% as per IS 2026 (Part 1))
Fault Current produced by the Inverters:
| No. Of Parallel Inverters (25kW) at ACCB |  |  |  | 16 | Nos
| Current Per Inverter |  |  |  | 36.2 | A
| Total Fault Current at Sixteen Inverters (If) |  |  |  | 724 | A
| Safety Factor (125 %) |  |  |  | 905 | A
| Corrosion Effect (1 % Every for 25 years) |  |  |  | 1131.25 | A
Area of Cross Section (A) = Fault Current (If) X Fault Current Time √(t)/ Material Constant (K)
| Area of Cross Section (A) = |  |  | 14.2946 | Sqmm
Where,
| If = | Fault Current (PV Side + Grid Side) |  |  | 1131.25 | Ampere
| t = | Fault Current time |  |  | 1 | Second
| K = | Material Constant |  |  | 79.1381
At AC Side the equipments will be connected by two 50x6 Strips by end to end.
Total cross section area of the strips is 600 Sqmm which is greater than the above required cross section.
Earth Strip Size Selected |  |  |  | 50X6 | Sqmm