## INV Earthing (hidden)
EARTHING DESIGN CALCULATION - INVERTER ROOM
INPUT DATA:
1) | Design Basis:
i) | Earth Electrode shall be GI pipe & main earth loop material shall be GI strip.
ii) | The earth conductor shall be adequately sized to carry the applicable maximum earth fault current
without undue temperature rise.
iii) | All the earth connections shall be made in accordance with IS: 3043.
2) | Reference:
i) | Code of Practice for Earthing (IS: 3043: 1987).
ii) | We have considered the highest fault level at the 33 kV level to be 25kA for 1 Sec.
iii) | Mean Electrical Soil Resistivity for the plant is considered as 100 Ohm-m (Average Condition assumed)
iv) | GI strip shall be of 50 x 6 mm.
3) | Assumptions
i) | Earthing conductor shall be buried under a depth of 60 cm from the ground level.
ii) | Electrode shall be 65mm dia, 3 M long GI Pipe as per IS 3043
4) | System Parameters
i) | Inverter Transformer Rating | = | 6000 | kVA | ( as maximum Inv. Trafo rating)
ii) | Operating Voltage | = | 33/ 0.400 | kV
iii) | Impedance of Transformer | = | 6.25 | %
iv) | Transformer Full Load Current on LV side | =
|  | = | 8660.5081 | A
v) | Through Fault Current at Transformer (I) | = | 25000 | A
vi) | Maximum opening time for VCB | = | 40 | msec.
during earth fault
vii) | Time considered for sizing the earth | = | 40+450 | msec.
| conductor | = | 490 | msec.
viii) | Mean Soil Resistivity, ρ | = | 100 | Ohm - m
ix) | Buried Earthing Conductor | = | 50 x 6 | GS flat
x) | Depth of Buried earthing, ω | = | 60 | cm
xi) | Width of the buried conductor (t) | = | 6.5 | cm
xii) | Total Length of the buried earthing | = | 15000 | cm
| conductor (l) |  | [Peripheral earthing and Branch Interconnections)
xiii) | Type of Electrode | = | 65mm dia, 3 m Long GI Pipe
xiv) | Number of Electrodes/ Inverter room | = | 10
5) | Calculation
i) | Check for Fault current withstand capability of selected earthing conductor
a) | Required cross section of Earthing | =
Conductor , A
(As per Cl.12.2.2.1 of IS: 3043)
where,
I = fault current for which fault of negliable impedance can flow through the device
K= factor dependent on the material of the protective conductor, the insulation and other parts, 80 for steel
T = time for fault clearing in sec.
b) | Required cross section of Earthing | = | 25000 X √0.49
80
|  | = | 218.75 | Sq.mm
c) | Corrosion factor (15%) | = | 251.5625 | Sq.mm
d) | Selected cross sectional of earthing conductor | = | 300 | Sq.mm
ii) | Calculation of Effective Resistance of buried earthing conductor (R cond )
a) | Resistance of Total buried earthing conductor, R cond = |  |  |  |  | ohm
( As per IS: 3043)
where, ρ indicates soil resistivity in ohm -m
l - Length of the earthing conductor in cm
ω- Depth of the earthing conductor in cm
t - width of the earthing conductor in cm.
| Resistance of the total buried earthing | = | 0.96876 | ohm
Conductor, Rcond
iii) | Calculation of Effective Resistance of Buried Electrode (Relec)
| Resistance of earth electrode is given by Relec | =
( As per IS: 3043)
where, ρ indicates soil resistivity in ohm -m
| d - diameter of the rod or pipe in cm | = | 300 | cm
| l - length of the rod or pipe in cm | = | 5 | cm
| Resistance of earth electrode is given by Relec | = | 25.3985 | Ohm
| Effective Resistance considering 10 Nos. of | = | 2.5398 | ohm
Electrodes
iv) | Calculation of Effective Earth Resistance for Inverter Room
| Effective Grid Resistance, R1 | =
|  | = | 0.70127 | ohm
6) | Result:
The above indicated Overall earthing system resistance for the Inverter room is less than 1 ohm
which meets the effective resistance of the system as per clause No: 20.1 of IS:3043. The selected
earthing conductor is suitable for withstanding the fault current and hence the design is safe

## PCSS & Sub PCSS (hidden)
EARTHING DESIGN CALCULATION - SUB PCSS & PCSS BUILDING
INPUT DATA:
| 1) | Design Basis:
| i) | Earth Electrode shall be 65mm Dia, 3Metre long Pipe Electrode.
| ii) | Buried Earth Grid shall be 50 x 8 mm G.I Flat Strip
| ii) | The earth conductor shall be adequately sized to carry the applicable maximum earth fault current
| iii) | All the earth connections shall be made in accordance with IS: 3043.
| 2) | Assumption:
| i) | Code of Practice for Earthing ( IS: 3043: 1987).
| ii) | We have considered the fault level of 25kA for designing the Earth Grid and system
| iii) | Mean Electrical Soil Resistivity for the plant is considered as 55 Ohm-m (Average Condition assumed)
| iv) | Earthing conductor shall be buried under a depth of 60 cm from the ground level.
| 4) | System Parameters
| i) | Through Fault Current at LT Switchboard | = | 25000 | A
| ii) | Maximum opening time for Breaker | = | 1 | sec.
during earth fault
| iv) | Mean Soil Resistivity, ρ | = | 100 | Ohm - m | Assumed 55 ohm-m for calculation purpose
| v) | Buried Earthing Conductor | = | 50 | mm G.I Flat Strip
| vi) | Depth of Buried earthing, ω | = | 60 | cm
| vii) | Width of the buried conductor (t) | = | 5 | cm
| vii) | Total Length of the buried earthing | = | 54400 | cm
conductor (l)
| viii) | Type of Electrode | = | 65mm dia, 3m Long G.I Pipe Electrode
| ix) | Number of Electrodes | = | 95
| 5) | Calculation
| i) | Check for Fault current withstand capability of selected earthing conductor
| a) | Required cross section of Earthing | =
Conductor , A
(As per Cl.12.2.2.1 of IS: 3043)
where,
I = fault current for which fault of negliable impedance can flow through the device
K= factor dependent on the material of the protective conductor, the insulation and other parts, 80 for steel
T = time for fault clearing in sec.
| b) | Required cross section of Earthing | = | 25000"X"√1
80
|  |  | = | 312.5 | Sq.mm
| c) | Corrosion factor (15%) | = | 359.375 | Sq.mm
| d) | Selected cross sectional of earthing conductor | = | 400 | Sq.mm
| ii) | Calculation of Effective Resistance of buried earthing conductor (R cond )
| a) | Resistance of Total buried earthing conductor, R cond = |  |  |  |  | ohm
( As per IS: 3043)
where, ρ indicates soil resistivity in ohm -m
|  | t - width (Strip) or twice the diameter (conductors in cm) |  | 5 | cm
|  | l - length of the rod or Strip in cm |  | 54400 | cm
|  | Resistance of the total buried earthing | = | 0.31249 | ohm
Conductor, Rcond
| iii) | Calculation of Effective Resistance of Buried Electrode (Relec) (65mm Dia G.I Pipe Electrode)
|  | Resistance of earth electrode is given by Relec | =
( As per IS: 3043)
where, ρ indicates soil resistivity in ohm -m
|  | d - diameter of the rod or pipe in cm | = | 6.5 | cm
|  | l - length of the rod or pipe in cm | = | 300 | cm
|  | Resistance of earth electrode is given by Relec | = | 24.0066 | Ohm
|  | Effective Resistance considering 95 Nos. of | = | 0.2527 | ohm
Electrodes
| iv) | Calculation of Effective Earth Resistance for Main Control Room
|  | Effective Grid Resistance, R2 | =
|  |  | = | 0.13972 | ohm
| 6) | Result:
The above indicated Overall earthing system resistance for the Sub PCSS & PCSS is less than 1 ohm
which meets the effective resistance of the system as per clause No: 20.1 of IS:3043. The selected
earthing conductor is suitable for withstanding the fault current and hence the design is safe

## Solar Field Earthing Calc_ShedA
EARTHING DESIGN CALCULATION - FLASYS DESIGN | [7 empty] | https://www.flasysdesign.com/
Email: contact@flasysdesign.com
INPUT DATA:
| 1) | Design Basis:
| i) | Earth Electrode shall be Chemical maintainance free earth pits & main earth loop material shall be GI strip.
| ii) | The earth conductor shall be adequately sized to carry the applicable maximum earth fault current
| iii) | All the earth connections shall be made in accordance with IS: 3043.
| 2) | Reference:
| i) | Code of Practice for Earthing ( IS: 3043: 1987).
| ii) | Mean Electrical Soil Resistivity for the plant is considered as 100 Ohm-m (Average Value)
| iii) | GI strip shall be of 25 x 6 mm.
| 3) | Assumptions
| i) | Earthing conductor shall be buried under a depth of 60 cm from the ground level.
| ii) | Electrode shall be 17.2mm dia, 3 M long Cu bonded steel rod (chemical earthing)
| 4) | System Parameters
| i) | Module / String Current Isc is (for 340Wp) | = | 9.53 | A
| ii) | Total number of strings/Inverter. | = | 18 | Nos | Max Isc possible
| iii) | Maximum Possibility of fault current that flows through the System DC Side | = | 205.848 | A
| iv) | Through Fault Current at DC Side | = | 205.848 | A
| v) | Maximum opening time DC Combiner box fuse | = | 0.2 | Sec
| vi) | Mean Soil Resistivity, ρ | = | 100 | Ohm - m | Assumed 100 ohm-m for calculation purpose
| vii) | Buried Earthing Conductor | = | 25 x 6 | GI flat
| viii) | Depth of Buried earthing, ω | = | 60 | cm
| ix) | Width of the buried conductor (t) | = | 2.5 | cm
| x) | Total Length of the earthing | = | 43900 | cm
conductor (l)
| xi) | Type of Electrode | = | 17.2mm dia, 3 m Long Cu Bonded rod
| xii) | Number of Electrodes | = | 4 | No. of earth electrode for complete plant
| 5) | Calculation
| i) | Check for Fault current withstand capability of selected earthing conductor
| a) | Required cross section of Earthing | =
Conductor , A
(As per Cl.12.2.2.1 of IS: 3043)
where,
I = fault current for which fault of negliable impedance can flow through the device
K= factor dependent on the material of the protective conductor, the insulation and other parts, 80 for steel
T = time for fault clearing in sec.
| b) | Required cross section of Earthing | = | 205.848" X "√0.2
80
|  |  | = | 1.1507 | Sq.mm
| c) | Corrosion factor (15%) | = | 1.3233 | Sq.mm
| d) | Selected cross sectional of earthing conductor | = | 150 | Sq.mm
| ii) | Calculation of Effective Resistance of buried earthing conductor (R cond )
| a) | Resistance of Total buried earthing conductor, R cond = |  |  |  |  | ohm
( As per IS: 3043)
where, ρ indicates soil resistivity in ohm -m
|  | l - length of the rod or Strip in cm |  | 43900 | cm
ω- Depth of the earthing conductor in cm
|  | t - width (Strip) or twice the diameter (conductors in cm) |  | 2.5 | cm
|  | Resistance of the total buried earthing | = | 0.40458 | ohm
Conductor, Rcond
| iii) | Calculation of Effective Resistance of Buried Electrode (Relec)
|  | Resistance of earth electrode is given by Relec | =
( As per IS: 3043)
where, ρ indicates soil resistivity in ohm -m
|  | d - diameter of the rod or pipe in cm | = | 1.72
|  | l - length of the rod or pipe in cm | = | 300
|  | Resistance of earth electrode is given by Relec | = | 31.0597 | Ohm
|  | Effective Resistance considering 4 Nos. of | = | 7.7649 | ohm
Electrodes
| iv) | Calculation of Effective Earth Resistance for Solar Field
|  | Effective Resistance, R3 | =
|  |  | = | 0.38455 | ohm
| v) | Calculation of Effective Earth Resistance for overall PV Plant
|  | Effective Resistance, Reff | = | (R1*R2*R3)/(R1+R2+R3)
|  | Effective Resistance for one Inverter room | = | 0.70127 | ohm
|  | For 3 No. of Inverter rooms | = | 0.16393 | ohm
|  | Effective Resistance for Control room-R2 | = | 0.13972 | ohm
|  | For 1 No. of Control rooms-R3 | = | 0.13972 | ohm
|  | Effective Resistance for Solar Field | = | 0.38455
|  | Overall PV Plant Effective Resistance | = | 0.012798 | Ohm
| 6) | Result:
The above indicated effective resistance of the plant is less than 1 ohm which meets the effective
resistance of the plant as per clause No: 20.1 of IS:3043. The selected earthing conductor is suitable for
withstanding the fault current and hence the design is safe

## Solar Field Earthing Calc_ShedB
EARTHING DESIGN CALCULATION - FLASYS DESIGN | [7 empty] | https://www.flasysdesign.com/
Email: contact@flasysdesign.com
INPUT DATA:
| 1) | Design Basis:
| i) | Earth Electrode shall be Chemical maintainance free earth pits & main earth loop material shall be GI strip.
| ii) | The earth conductor shall be adequately sized to carry the applicable maximum earth fault current
| iii) | All the earth connections shall be made in accordance with IS: 3043.
| 2) | Reference:
| i) | Code of Practice for Earthing ( IS: 3043: 1987).
| ii) | Mean Electrical Soil Resistivity for the plant is considered as 100 Ohm-m (Average Value)
| iii) | GI strip shall be of 25 x 6 mm.
| 3) | Assumptions
| i) | Earthing conductor shall be buried under a depth of 60 cm from the ground level.
| ii) | Electrode shall be 17.2mm dia, 3 M long Cu bonded steel rod (chemical earthing)
| 4) | System Parameters
| i) | Module / String Current Isc is (for 340Wp) | = | 9.53 | A
| ii) | Total number of strings/Inverter. | = | 18 | Nos | Max Isc possible
| iii) | Maximum Possibility of fault current that flows through the System DC Side | = | 205.848 | A
| iv) | Through Fault Current at DC Side | = | 205.848 | A
| v) | Maximum opening time DC Combiner box fuse | = | 0.2 | Sec
| vi) | Mean Soil Resistivity, ρ | = | 100 | Ohm - m | Assumed 100 ohm-m for calculation purpose
| vii) | Buried Earthing Conductor | = | 25 x 6 | GI flat
| viii) | Depth of Buried earthing, ω | = | 60 | cm
| ix) | Width of the buried conductor (t) | = | 2.5 | cm
| x) | Total Length of the earthing | = | 29000 | cm
conductor (l)
| xi) | Type of Electrode | = | 17.2mm dia, 3 m Long Cu Bonded rod
| xii) | Number of Electrodes | = | 2 | No. of earth electrode for complete plant
| 5) | Calculation
| i) | Check for Fault current withstand capability of selected earthing conductor
| a) | Required cross section of Earthing | =
Conductor , A
(As per Cl.12.2.2.1 of IS: 3043)
where,
I = fault current for which fault of negliable impedance can flow through the device
K= factor dependent on the material of the protective conductor, the insulation and other parts, 80 for steel
T = time for fault clearing in sec.
| b) | Required cross section of Earthing | = | 205.848" X "√0.2
80
|  |  | = | 1.1507 | Sq.mm
| c) | Corrosion factor (15%) | = | 1.3233 | Sq.mm
| d) | Selected cross sectional of earthing conductor | = | 150 | Sq.mm
| ii) | Calculation of Effective Resistance of buried earthing conductor (R cond )
| a) | Resistance of Total buried earthing conductor, R cond = |  |  |  |  | ohm
( As per IS: 3043)
where, ρ indicates soil resistivity in ohm -m
|  | l - length of the rod or Strip in cm |  | 29000 | cm
ω- Depth of the earthing conductor in cm
|  | t - width (Strip) or twice the diameter (conductors in cm) |  | 2.5 | cm
|  | Resistance of the total buried earthing | = | 0.5897 | ohm
Conductor, Rcond
| iii) | Calculation of Effective Resistance of Buried Electrode (Relec)
|  | Resistance of earth electrode is given by Relec | =
( As per IS: 3043)
where, ρ indicates soil resistivity in ohm -m
|  | d - diameter of the rod or pipe in cm | = | 1.72
|  | l - length of the rod or pipe in cm | = | 300
|  | Resistance of earth electrode is given by Relec | = | 31.0597 | Ohm
|  | Effective Resistance considering 2 Nos. of | = | 15.5298 | ohm
Electrodes
| iv) | Calculation of Effective Earth Resistance for Solar Field
|  | Effective Resistance, R3 | =
|  |  | = | 0.56813 | ohm
| v) | Calculation of Effective Earth Resistance for overall PV Plant
|  | Effective Resistance, Reff | = | (R1*R2*R3)/(R1+R2+R3)
|  | Effective Resistance for one Inverter room | = | 0.70127 | ohm
|  | For 3 No. of Inverter rooms | = | 0.16393 | ohm
|  | Effective Resistance for Control room-R2 | = | 0.13972 | ohm
|  | For 1 No. of Control rooms-R3 | = | 0.13972 | ohm
|  | Effective Resistance for Solar Field | = | 0.56813
|  | Overall PV Plant Effective Resistance | = | 0.014926 | Ohm
| 6) | Result:
The above indicated effective resistance of the plant is less than 1 ohm which meets the effective
resistance of the plant as per clause No: 20.1 of IS:3043. The selected earthing conductor is suitable for
withstanding the fault current and hence the design is safe