## earthing calculation
S.NO. | EARTHING CALCULATION DC | [6 empty] | https://www.flasysdesign.com/
Email: contact@flasysdesign.com
ESTIMATION OF DC SIDE EARTHING
| ENTER SOIL RESTIVITY ῤ= |  |  | 50 | ῼm
1 | CALCULATING THE EARTHING STRIP SIZE
| ENTER THE Isc OF THE SELECTED MODULE |  |  |  | 9.02 | Amps
| ENTER THE NO. OF STRINGS CONNECTED TO THE INVERTER |  |  |  | 4 | NO.
ESTIMATING THE SHORT CIRCUIT CURRENT THAT CAN FLOW IN THE DC SIDE EARTHING SYSTEM
Isc=Isc OF THE SELECTED PV MODULE*NO. OF STRING CONNECTED TO THE INVERTER*1.25 (1.25 IS THE DESIGN MARGIN)
| SO, Isc= |  | 45.1 | Amps
NOW USING THE conductor sizing FORMULA
A=(Isc*√t)/k
HERE t= THE OPERATING TIME OF THE DISCONNECTING DEVICE
k, IS THE CURRENT RATING OF THE VARIOUS PROTECTIVE EARTHING MATERIAL
CONSIDER THE TABBLE BELOW
CURRENT RATING OF VARIOUS PROTECTIVE EARTHING MATERIALS Amps
| TIME/MATERIAL |  |  | COPPER | ALUMINIUM | STEEL
| 1sec CURRENT RATING Amps/mm² |  |  | 205 | 126 | 80
| 3sec CURRENT RATING Amps/mm² |  |  | 118 | 73 | 46
| ENTER THE SELECTED VALUE OF t = |  |  |  | 3 | sec
| ENTER THE SELECTED VALUE OF k= |  |  |  | 46 | Amps
| THEREFORE THE CALCULATED CONDUCTER SIZE IS "A"= |  |  |  |  | 1.6982 | mm²
STANDARD VALUE AVAILABLE IN THE MARKET
25*3 mm² G.I. STRIP i.e 75 mm²
FOR APPLICABLE CORROSION FACTOR OF 15% FROM THE FOLLOWING TABLE:
| TYPE OF LAYING OF THE EARTH CONDUCTOR |  |  | ALLOWANCE TO BE CONSIDERED
| CONDUCTORS LAIED TO SOIL HAVING RESISTIVITY GREATER THAN 100 ohm-meters |  |  | 0% corrosion
| CONDUCTORS LAIED TO SOIL HAVING RESISTIVITY from 25 to 100 ohm-meters |  |  | 15% corrosion
| conductor laid in soil having resistivity lower than 25ohm-meters |  |  | 30% corrosion
| enter the selected corrosion factor from above table = |  |  |  |  | 15 | %
[5 empty] | i.e. | 1.15 | CF
now multiplying the value of "A" with corrosion factor CF
|  | so A= | 1.9529 | mm²
2 | Now Earth resistance due to earthing pit is given as :
where "L" is the length of the GI pipe
and "d" is the diameter of the pipe
where R1 is the equivalent resistance / no. of earth pits
| ENTER THE VALUE OF L= |  |  | 300 | cm
| ENTER THE VALUE OF d = |  |  | 2.5 | cm
| SO R= | 16.3848 | ῼ
| enter the no. of earthing pits for inverter |  |  |  | 2
| enter the no. of earthing pits for ACDB |  |  |  | 2
| TOTAL EARTHING PITS |  |  | 4
HENCE EQUIVALENT RESISTANCE OF INDIVIDUAL PIT IS = R1/NO. OF PITS
| HENCE EQUIVQLENT R1= |  |  | 4.0962 | ῼ
3 | EARTHING RESISTANCE DUE TO EARTHING STRIP
where "L" is the length of the GI STRIP
where "W" is the depth of burial of electrode
where "t" is the width of the strip
| ENTER THE VALUE OF L= |  |  | 20000 | cm
| ENTER THE VALUE OF W= |  |  | 300 | cm
| ENTER THE VALUE OF t= |  |  | 2.5 | cm
| SO R2= | 0.55255 | ῼ
HENCE R2 IS THE EQUIVALENT RESISTANCE DUE TO HORIZONTAL AND VERTICAL ELECTRODE
Since the horizontal and vertical electrode are interconnected in parallel arrangement , the equivalent resistance of the PV yard is computed by the following formula
| so, (R)parallel = |  | 0.48687 | ῼ
note : the value of (R)parallel should be less than 1ῼ for a propper earthing.