## Earthing
|  |  |  | SUBSTATION EARTHING DESIGN |  |  |  |  | https://www.flasysdesign.com/
Email: contact@flasysdesign.com
Input data :- | [12 empty] | Description | Material conductivity (%) | αr factor at 20°C (1/°C) | Ko at 20°C | temperature Tm (°C) | ρr 20°C (μΩcm) | TCAP thermal capacity [J/(cm3. °C)]
[13 empty] | Copper annealed soft drawn | 100 | 0.00393 | 234 | 1083 | 1.72 | 3.42
1 | Conductor material |  | = | Steel, 1020 |  | 18 | Length of one earth mat conductor Lx |  |  | = | 100 | metre | Copper commercial hard drawn | 97 | 0.00381 | 242 | 1084 | 1.78 | 3.42
[13 empty] | Copper-clad steel wire | 40 | 0.00378 | 245 | 1084 | 4.4 | 3.85
2 | System Voltage |  | = | 132 | kV | 19 | Width of one earth mat conductor Ly |  |  | = | 50 | metre | Copper-clad steel wire | 30 | 0.00378 | 245 | 1084 | 5.86 | 3.85
[13 empty] | Copper-clad steel rodb | 20 | 0.00378 | 245 | 1084 | 8.62 | 3.85
3 | Fault Current, If |  | = | 31.5 | kA | 20 | Additional length of conductor considered |  |  |  | 12 | metre | Aluminum EC Grade | 61 | 0.00403 | 228 | 657 | 2.86 | 2.56
[13 empty] | Aluminum 5005 alloy | 53.5 | 0.00353 | 263 | 652 | 3.22 | 2.6
4 | Fault Duration, tc |  | = | 1 | sec | 21 | Grid conductor combined length, Lc |  |  | = | 3162 | metre | Aluminum 6201 alloy | 52.5 | 0.00347 | 268 | 654 | 3.28 | 2.6
[13 empty] | Aluminum-clad steel wire | 20.3 | 0.0036 | 258 | 657 | 8.48 | 3.58
5 | Max. Allowable Temperature, Tm |  | = | 1510 | 0C | 22 | Total no. of ground rods (Untreated) | [5 empty] | Steel, 1020 | 10.8 | 0.0016 | 605 | 1510 | 15.9 | 3.28
[7 empty] | SA |  |  |  | 0 |  | stainless-clad steel rodc | 9.8 | 0.0016 | 605 | 1400 | 17.5 | 4.44
6 | Ambient Temperature, Ta |  | = | 50 | 0C |  | Transformers (Body earthing) |  |  |  | 1 |  | Zinc-coated steel rod | 8.6 | 0.0032 | 293 | 419 | 20.1 | 3.93
[7 empty] | Towers with peak |  |  |  | 1 |  | Stainless steel | 2.4 | 0.0013 | 749 | 1400 | 72 | 4.03
7 | Reference temp for material constant,Tr |  | = | 20 | 0C |  | Switchyard corners |  |  |  | 1 |  | weight
[7 empty] | Additional ground rods |  |  |  | 1 |  | 50
8 | Thermal Co-eff.of resistivity at reference | [5 empty] | Total no of rods |  |  |  | 4 |  | 70
| Temperature, ar |  | = | 0.0016 |  | 23 | length of each rod in m Lr |  |  | = | 3 | meter
[7 empty] | Total ground rod length, LR |  |  | = | 12 | metre
9 | Resistivity of Ground Conductor at ref.
| Temperature, rr |  | = | 15.9 | mW/cm3 | 24 | Effective length of buried conductor |  |  | = | 3174 | metre
LT = LR + Lc
10 | Thermal Capacity Factor, TCAP |  | = | 3.28 | J/cm3/oC | 25 | Soil Resistivityconsidered for design, r |  |  | = | 49.12 | W-meter
11 | K0 = (1/ar) -Tr |  | = | 605 |  | 26 | Surface Resistivity, rs |  |  | = | 3000 | W-meter
12 | Length of Earth grid |  | = | 100 | metre | 27 | Spacing for Earthing Mat ,D |  |  | = | 4 | meter
13 | Width of Earth grid |  | = | 50 | metre | 28 | Corrective weighting factor, Kii |  |  | = | 1
14 | Area of Earth grid, A |  | = | 5000 | sq.metre | 29 | Reference Depth of grid, h0 |  |  | = | 1 | meter
15 | Depth of burial w.r.t. ground level, h |  | = | 1 | metre | 29 | Thickness of Concrete , hs |  |  | = | 0.15 | meter
16 | Calculate w.r.t to person weight(50/70) |  | = | 50 | Kg | 30 | Fault Current division factor (Sf) |  |  | = | 0.5
17 | No. of conductors parallel to length side( nl) |  | = | 25 |  | 31 | No. of conductors parallel to width side ( ns) |  |  | = | 13
Output:
| Conductor size, A |  | = | 231.0226 | SQMM |  | Effective Buried Length for mesh voltage, LM |  |  | = | 3180.9928 | Meter
| By considering 30% allowance |  | = | 300.3294 | SQMM |  | Effective Buried Length for step voltage, LS |  |  | = | 2381.7 | Meter
|  | A | = | 300 | SQMM
[7 empty] | Grid Resistance |  |  | = | 0.25771 | Ohms
| Ground Potential Rise(GPR) |  | = | 4058.8997 | Volts
| Tolerable | [5 empty] | Tolerable
| Touch Voltage Etouch |  | = | 734.6992 | Volts |  | Step Voltage Estep |  |  | = | 2446.6507 | Volts
| Attainable | [5 empty] | Attainable
| Touch Voltage Etouch |  | = | 701.2088 | Volts |  | Step Voltage Estep |  |  | = | 379.056 | Volts
|  |  | As per the above Design the System is |  |  |  |  | SAFE

## Calculations
https://www.flasysdesign.com/
Conductor Size :- | [9 empty] | Email: contact@flasysdesign.com
As per Eq.37 of IEEE Std 80-2000, conductor size is given by
tc ar rr x 104
TCAP
A | = | If |  | Ko + Tm
ln 1 +
Ko + Ta
2.2) | Calculation of Tolerable Etouch & Estep Voltage :
a) | Tolerable Etouch :
From IEEE Std 80-2000
For | 50 | Tolerable Etouch50= |  | [(1000 + 1.5CS rS) 0.116/ ÖtS ] |  |  | ( From eq.32of IEEE Std 80-2000 )
For | 70 | Tolerable Etouch70= |  | [(1000 + 1.5CS rS) 0.157/ ÖtS ]
Where,
Cs = Reduction factor for derating the nominal value of surface layer
resistivity.
|  | Cs = 1 - 0.09 [(1-r/rs)/(2hs + 0.09)] |  |  |  | ( From eq.27 of IEEE Std 80-2000 )
|  | Cs | = | 0.77301
|  | tS = Duration of shock current in seconds = |  |  |  | 0.5
( from clause 16.2.2 of IEEE Std 80-2000 )
Substituting the above values,
| Tolerable Etouch50 |  | = | 734.6992 | Volts
| Tolerable Etouch70 |  | = | 994.3774 | Volts
b) | Tolerable Estep | [5 empty] | (from eq.29 of IEEE Std 80-2000)
For | 50 | Tolerable Estep50 = |  | [(1000 + 6CS rS) 0.116/ ÖtS ]
For | 70 | Tolerable Estep70 = |  | [(1000 + 6CS rS) 0.157/ ÖtS ]
Substituting the values,
| Tolerable Estep50 |  | = | 2446.6507 | Volts
| Tolerable Estep70 |  | = | 3311.4151 | Volts
2.3) | Calculation of Grid Resistance, Rg :
As per IEEE Std 80-2000,
R1 R2 - Rm2
| The total system resistance, Rg |  |  | =
R1 + R2 - 2Rm
Where,
| R1 | = | Ground resistance of grid conductors in Ω
| R2 | = | Ground resistance of of all ground rods in Ω
| Rm | = | Mutual ground resistance between the group of grid conductors, R1 and
group of ground rods, R2 in Ω
Ground resistance of the grid, R1
|  |  | ρ | 2 Lc | k1 Lc
| R1 | = | ln |  | + | - k2 | From IEEE Std 80-2000
|  |  | ΠLc | a' | A
|  | a | = | 0.019549
Where,
| r | = | Soil Resistivity in Ω-m |  |  |  |  | 49.12 | ohm-m
| Lc | = | Total length of all connected grid conductors in m |  |  |  |  | 3162 | m
| a' | = | a.2h | for conductors buried at depth h in m |  |  |  | 0.19773 | m
| 2a | = | Diameter of conductor in m |  |  |  |  | 0.019549 | m
| A | = | Area covered by conductors in m2 |  |  |  |  | 5000 | m2
| k1 | = | Coefficient from fig 25(a) of IEEE Std 80-2000 |  |  |  |  | 1.03
k1= -0.05*(Lx/Ly) + 1.13
| k2 | = | Coefficient from fig 25(b) of IEEE Std 80-2000 |  |  |  |  | 4.3
k2= -0.05*(Lx/Ly) + 4.40
Coefficient K1 and k2 of schwarz's fromula IEEE Std 80-2000 )
| R1 | = | 0.25778 | Ω
Ground resistance of the rod bed, R2
From eq.55 of IEEE Std 80-2000
|  |  | r | 4 LR | 2 k1 . Lr
| R2 | = |  | ln | -1 + | ( nR - 1 )2
|  |  | 2p nRLR | b | A
Where,
| Lr | = | length of each rod in m |  |  | 3 | m
| 2b | = | diameter of rod in m |  |  | 0.019549 | m
| nR | = | number of rods placed in area A |  |  | 4
| LR | = | Total length of ground rods |  |  | 12
| k1 | = | Coefficient from fig 25(a) of IEEE Std 80-2000 |  |  |  |  | 1.03
| R2 | = | 1.2356 | Ω
Mutual ground resistance between the grid and the rod bed, Rm
From eq.56 of IEEE Std 80-2000
|  |  | r | 2 Lc | k1 Lc
| Rm | = | ln |  | + | - k2 + 1
|  |  | p Lc | Lr | A
| Rm | = | 0.24928 | Ω
Subtituting the above values,
| Rg | = | 0.25771 | Ω
2.4) | Calculation of Maximum Ground Potential Rise :
| Max. Ground potential above remote earth, GPR |  |  |  |  | = | IG x RG | Volts
Where,
|  | IG = grid current |  | = | If x Sf
|  |  | IG | = | 15.75 | KA
Substituting the values,
| Ground Potential Rise, GPR |  |  | = | 4058.8997 | Volts
Since, GPR > Estep50 (as per Figure 33 of IEEE Std 80-2000),calculate Attainable Emesh and Attainable
Estep voltages
2.5) | Calculation of Attainable Emesh Voltage :
From Eq.80 of IEEE Std 80-2000, for Grid rods in the periphery,
Emesh = [ r Km Ki IG / LM ]
Lr
|  | LM = Lc + | 1.55+1.22 |  | Lr | From eq.91 of IEEE Std 80-2000
L2x + L2y
Where,
| Lr | = | Length of each ground rod |  |  |  | = | 3 | m
| Lx | = | Maximum length of grid conductor in x-direction = |  |  |  |  | 100 | m
| Ly | = | Maximum length of grid conductor in y-direction = |  |  |  |  | 50 | m
| IG | = | grid current |  |  |  | = | 15.75
| Ki | = | corrective Factor, |  |  |  | = | 3.8571
p1
| LR | = | Total length of ground rods |  |  |  | = | 12 | m
Subtituting the above values,
| LM | = | 3180.9928 | m
As per Eq.81 of IEEE Std 80-2000, the Spacing Factor for Mesh Voltage,
|  | 1 | D2 | (D + 2h)2 | h | Kii | 8
| Km = | ln | + |  | - | + ln
|  | 2p | 16hd | 8Dd | 4d | Kh | p(2n-1)
| Equ. Diameter of Earth conductor, d |  |  |  | = | 0.017151 | metre
| Kh = 1 + h / h0 |  | ( From eq.83 of IEEE Std 80-2000 )
|  | Kh |  |  | = | 1.4142
| No. of Parallel Paths, n |  |  |  | = | na nb nc nd | (From eq.84 of IEEE Std 80-2000)
| Where, | From eq.85 to 88 of IEEE Std 80-2000 |  |  |  |  | Lp
|  | na | = | (2 Lc)/Lp | nb | =
4 A
0.7 A
|  |  |  | Lx Ly | Lx Ly |  | Dm
|  | nc | = |  | nd | I
|  |  |  | A |  |  | L2x + L2y
Where,
| Lp | = | Peripheral length of the grid |  |  |  | = | 300 | m
| Dm | = | Maximum distance between any two points
|  |  | on the grid |  |  |  | = | 111.8034 | m
Substituting the above values,
| na | = | 21.08 | nb | = | 1.0299
| nc | = | 1 | nd | = | 1
| n | = | 21.7099 |  | = | 21.7099 | Rounded of to nearest digit
As per Eq.89 of IEEE 80-2000,
|  | The corrective Factor, Ki |  |  | = | 0.644 + ( 0.148 x n ) |  | From eq.89of IEEE Std 80-2000
[5 empty] | = | 3.8571
Substituting the values,
|  |  |  | Km | = | 0.7475
|  | Attainable | Emesh Voltage |  | = | 701.2088 | Volts
2.6) | Calculation of Attainable Estep voltage :
From Eq.92 of IEEE Std 80-2000,
|  |  |  | Attainable Estep = [ r Ks Ki IG / LS ] |  |  |  | From eq.92 of IEEE Std 80-2000
As per Eq.94 of IEEE Std 80-2000, the Spacing Factor for Step Voltage,
|  | 1 1 | 1 | 1
| Ks = | + | + | (1 - 0.5n-2) |  | From eq.94of IEEE Std 80-2000
|  | P 2h | D + h | D
| No. of Parallel paths, n |  |  |  | = | 21.7099
|  |  |  | n | = | 21.7099
As per Eq.89 of IEEE 80-2000,
|  | The corrective Factor, Ki |  |  | = | 0.644 + ( 0.148 x n )
|  |  |  | Ki | = | 3.8571
|  |  |  | Ks | = | 0.30255
As per Eq.93 of IEEE Std 80-2000,
| Ls | = | 0.75 Lc + 0.85 LR |  | From eq.93of IEEE Std 80-2000
| Lc | = | Total length of all connected grid conductors in m
| LR | = | Total length of ground rods
| Ls | = | 2381.7 | m
Substituting the values,
|  | Attainable Estep |  |  | = | 379.056 | Volts
| SAFE |  | SAFE
NOT SAFE