## Front Sheet-Potrait
https://www.flasysdesign.com/
Email: contact@flasysdesign.com
Earthing & Lightning Protection Calculation
Contractor:
Client:
Location:
Job No.:
APG Project No:
Rev | Date | Status | Document Status | Prepared by |  | Checked By | Approved By
Page : 1 of 9

## Hold Sheet-Potrait
Earthing & Lightning Protection Calculation
Record of Revisions
Rev. | Date | Revision Details
Table of Holds
The following holds have been identified. They will be cleared as soon as practicable.
Section |  | Details of Hold | Hold Cleared (rev)
Page 2 of 9

## Index
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [9 empty] | Email: contact@flasysdesign.com
TABLE OF CONTENTS
Section-1 : Earthing Study
| 1 | Scope |  |  |  | 4
| 2 | Reference documents |  |  |  | 4
| 3 | Design inputs |  |  |  | 4
| 4 | Formulae |  |  |  | 4
| 5 | Calculations |  |  |  | 6
|  | A | Main earth grid GI strip sizing |  |  | 6
|  | B | Plant earth grid GI strip sizing |  |  | 6
|  | C | Calculation of number of earth electrodes |  |  | 7
|  | D | System resistance |  |  | 8
|  | E | Grid resistance |  |  | 8
| 6 | Conclusion |  |  |  | 8
| 7 | Recommendations |  |  |  | 8
Section-2 : Lightning Study
| 1 | Scope |  |  |  | 1
| 2 | Reference documents |  |  |  | 1
| 3 | Design inputs |  |  |  | 1
| 4 | Formulae |  |  |  | 1
| 5 | Calculation for Requirement of LPS |  |  |  | 2
|  | A | Substation Building |  |  | 2
|  | B | Plant Interface Building (PIB) |  |  | 3
|  | C | Maintenance Building |  |  | 4
|  | D | Catalyst Storage Building |  |  | 5
|  | E | LPS For Metallic Structures/Buildings |  |  | 6
| 6 | Summary |  |  |  | 7
|  | Annexure-1 -- Fault current calculation |  |  |  | -
[5 empty] | Page |  | 3 | of | 9

## Sheet 1
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [14 empty] | Email: contact@flasysdesign.com
Section-1 : Earthing Study
| 1 | Scope:
This section of document covers the calculation to determine the size of main earth strip & number of total earth electrodes required for
the earthing system .
| 2 | Reference Documents:
This calculation is based on following documents :
| 3 | Design Inputs:
1> Soil Resistivity is taken as 45 ohm-m as per Clause no 11 (Page 25 of 42) of Ref Documents as mentioned under 5> above.
2> Depth of pipe electrode in contact with earth is considered as pipe length = 3 m
3> For earth grid design, duration of fault current considered is 0.5 sec as per Electrical Design Basis.
|  | 4> | 11kV System : Resistance earthed by 250A NER.
6.6kV System : Resistance earthed by 250A NER.
0.415kV & 0.690kV System : Solidly earthed.
5> Material of earth electrode is considered as 100NB Class 'B' GI pipe Electrode ‐ 3m long as per Standard Specifiaction for Cable Trays &
earthing Material.
| 4 | Formulae:
4.1. Resistance of pipe electrode (ref. 9.2.2. of IS: 3043 - Amend No. 2)
|  |  | Re | = | [100р/2Лl] x [loge (2l/d)] ohm
|  |  | where, |  | l = length of pipe in cm.
d = diameter of pipe in cm
р = resistivity of soil in ohm-m
4.2. Permissible current density for given value of soil resistivity & for given duration (ref. 10.3 of IS: 3043)
|  |  |  | J = |  | 7.57 x 103
Ört
where t = duration of fault (sec)
4.3. The cross-sectional area of earthing conductor for disconnection time not exceeding 5 sec (ref. 12.2.2.1 of IS: 3043)
|  |  |  | 1/S = | K | * | 1 / I Öt
where,
S = cross sectional area in sq.mm.
I = r.m.s. value of fault current of system in amperes
K = factor from IS: 3043 table 6.
|  |  | Table 6A | [5 empty] | Table 6D
|  |  | Bare Conductor with No Risk of Fire or Danger | [5 empty] | Protective Bare Conductors in Hazardous Areas Where There is Risk
|  |  | to Any Other Touching or Surrounding Material | [5 empty] | of Fire from Petroleum Bound Oil or Other Surrounding Material
|  |  | Copper |  |  |  | 205 |  | Copper | 153
|  |  | Aluminium |  |  |  | 126 |  | Aluminium | 101
|  |  | Steel |  |  |  | 80 |  | Steel | 56
[11 empty] | Page | 4 | of | 9

## Sheet 2
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [20 empty] | Email: contact@flasysdesign.com
| 4.4 |  | Inputs:
| 1 | : Maximum Fault Current (for Main Earth grid sizing) | [5 empty] | (LV Switchboard / PCC design fault current) | [7 empty] | 65 |  |  |  | kA
|  | : Maximum Fault Current (for Plant Earth grid sizing) | [5 empty] | (Refer - Annexure-1) * | [7 empty] | 15.4451 |  |  |  | kA
| 2 | : Duration of Fault (Fault Clearing Time) | [13 empty] | 0.5 |  |  |  | Sec.
| 3 | : Average soil resistivity | [13 empty] | 45 |  |  |  | Ohm-m
| 4 | : Pipe electrode length (l) | [13 empty] | 300 |  |  |  | cm
| 5 | : Pipe electrode length in contact with ground (l) | [13 empty] | 300 |  |  |  | cm
| 6 | : Pipe electrode diameter (D) | [13 empty] | 10 |  |  |  | cm
| 7 | : Corrosion allowance for GI strip | [5 empty] | (As per Design Basis CL No. 8.10) | [7 empty] | 30 |  |  |  | %
* 11kV & 6.6kV Systems are resistively earthed with NGR rating 250A. Therefore plant earthing is designed considering Maximum earth
fault current on 415V & 690V system 15.45kA as calculated in Annexure-1.
| 4.5 |  | Symbols
| I | : Fault Current in kA | [13 empty] | 65
| t | : Fault duration in seconds | [13 empty] | 0.5
| K | : Constant (for GI Earth strip in safe area) |  |  |  | (ref. Table 6A of IS 3043:1987) | [9 empty] | 80
|  | (for GI Earth strip in Hazardous area) |  |  |  | (ref. Table 6D of IS 3043:1987) | [9 empty] | 56
| w | : Depth of burial of the strip in cm |  |  |  | (ref. Cl 20.6.3.2 of IS 3043:1987) | [9 empty] | 60
| t | : Width of strip in cm | [13 empty] | 7.5
| 4.6 |  | Estimated Strip Laid Area (Substation): | [5 empty] | Estimated Strip Laid Area (Plant):
|  | Strip laid 600mm below ground over (Approx) |  |  |  | 250 | mtr |  | Strip laid 600mm below ground over (Approx) | [9 empty] | 2260 | mtr
N
|  |  |  | 32 | [17 empty] | 530
|  |  |  | Substation | 80 | [16 empty] | 390
[13 empty] | 150 |  |  | 130 | [5 empty] | 195
[10 empty] | 269 |  | 269 | [9 empty] | 385
[13 empty] | 150 | [8 empty] | 120
[14 empty] | 195 | [7 empty] | 120
175
[11 empty] | - Plot | [10 empty] | 170
[11 empty] | 296 | [6 empty] | NTS |  |  |  | 175
NTS
|  | Earth Grid around the Substation | [7 empty] | Earth Grid around the Plot & below Piperacks
|  | (Approx length for calculation purpose only) | [7 empty] | (Approx length for calculation purpose only)
[14 empty] | Page | 5 |  | of |  | 9

## Sheet 3
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [19 empty] | Email: contact@flasysdesign.com
| 5 | Calculation:
| A | Main Earth Grid GI Strip Sizing (Around Substation)
Cross sectional area of Main earth strip (GI) required to carry the rated fault current for 0.5 sec
Design fault level for LV Switchboard / PCC is 65 kA for 1sec.
Hence Main earth strip shall be designed for this fault current
|  |  | 1/S = | K | * | 1 / I Öt
|  | K= | 80 |  |  |  | (for Non hazardous area near Substation)
|  | S = | I/K | * | Öt |  | = | 65 * 1000 * |  |  | Ö 0.5
80
|  | = | 574.5243
|  | Required Cross sect. area of GI strip = | [9 empty] | 575 |  |  | sq.mm
|  | Considering 30% Corrosion allowance : | [9 empty] | 747.5 |  |  | sq.mm
|  | Since Cross sect area of 75 x 10mm GI Stip = | [9 empty] | 750 |  |  | sq.mm
[12 empty] | 75 x 10 |  |  | mm GI strip to be selected
Therefore, Earth grid around Substation shall be by 75 x 10mm GI earth Strip
| B | Plant Earth Grid GI Strip Sizing
The max. earth fault current to be dessipated by plant earth grid is same as that of the earth fault current of the largest kW motor
(LV) located near the source. Refer Annexure-1 for earth fault current calculation of SEED BED BLOWER MOTOR
(Tag no. MA-CHC501-M5613, 5614) of rating 225 kW on 415V system & PELLET WATER PUMP MOTOR (Tag no. MP-CHC501-M7012 /
7017) of rating 250kW on 690V system.
Max Cross sectional area of Plant earth strip (GI) required to carry the fault current of 15.45 kA for 0.5 sec is calculated as follows,
|  |  |  | 1/S = | K | * | 1/ I Öt
|  |  | K= | 56 |  |  |  | (for hazardous area)
|  |  | S = | I/K | * | Öt |  |  |  | = | 15.45 * 1000 |  | * Ö 0.5
56
|  |  | = | 195.0237
|  |  | Required Cross sect. area of GI strip = | [10 empty] | 196 |  | sq.mm
|  |  | Considering 30% Corrosion allowance: | [10 empty] | 254.8 |  | sq.mm
|  |  | Since Cross sect area of 50 x 6mm GI Stip = | [10 empty] | 300 |  |  | sq.mm
[14 empty] | 50 x 6 |  | mm GI earth strip may be selected.
However for Standardization purpose, Earth grid for Plant shall be by selected as 75 x 10mm GI earth Strip
[18 empty] | Page | 6 | of | 9

## Sheet 4
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [28 empty] | Email: contact@flasysdesign.com
C | Calculation for Number of Earth Electrodes:
1. Resistance to pipe electrode
|  |  | r | = | 45 |  |  |  | ohm-m
|  |  | l | = | 300 |  |  |  | cm (length in contact with ground)
|  |  | d | = | 10 |  |  |  | cm
|  |  | Re | = | [100р/2Лl] x [loge (2l/d)] ohm
|  |  |  | = | 9.7745 |  |  |  | ohm
|  | In order to achieve an overall earth resistance below 1 ohm, | [14 empty] | 10 |  |  | nos min. pipe electrodes are required.
|  | 2. Permissible current density for given value of soil resistivity & for given duration of | [18 empty] | 0.5 |  | sec.
|  |  | J | = | 7.57 x 103 |  |  |  | A/sq.m
Ört
|  |  | r | = | 45 |  |  |  | ohm-mtr
|  |  | t | = | 0.5 |  |  |  | sec
|  |  | J | = | 1595.8961 |  |  | A/sq.m
3. Total area of each pipe electrode in contact with ground
[5 empty] | A | = | pDl
[6 empty] | = | 0.94248 |  |  | sq. m
Considering 5% reduction in the gross area of pipe electrodes due to perforations & also tapering of pipe electrodes at bottom.
|  | Hence net area of each pipe electrode | [9 empty] | 0.89535 |  |  | sq.m.
4. Total surface area of pipe electrode required for fault current dissipation =
Fault current component in amperes for dissipation through earthing elements
current density in A/sq.m
[16 empty] | Substation | [7 empty] | Plant
|  | Total Fault kA | [10 empty] | = | 65 |  | kA | [5 empty] | 15.4451 |  | kA
|  | Current Density | [10 empty] | = | 1595.8961 |  | A/sq.m | [5 empty] | 1595.8961 |  | A/sq.m
|  | Total surface area of earth elements required | [10 empty] | = | 40.7295 |  | sq.m | [5 empty] | 9.678 |  | sq.m
5. Minimum Total number of pipe electrode required to be interconnected for Plot spread
|  | Total Earth Electrode Area | [9 empty] | = | 40.7295 |  |  | sqm |  | (Max of the surface area calculated above in 4.)
|  | Considering corrossion allowance : | [9 empty] | = | 52.9483 |  |  | sqm
|  | Area of each earth electrode | [9 empty] | = | 0.89535 |  |  | sqm
|  | Total no. of earth electrodes | [9 empty] | = | 59.1367 |  |  | Nos.
|  | In order to achieve an overall earth resistance below 1 ohm & dessipation of 65kA of earth fault current, min | [22 empty] | 60 |  |  | Nos.
electrodes will be required.
6. Earth Strip Areas =
|  | Substation | [15 empty] | Plant
|  | Area of Strip in contact with ground | [8 empty] | 250 * {(75 * 2) + (10 *2)} | [6 empty] | Area of Strip in contact with ground | [5 empty] | 2260 * {(75 * 2) + (10 *2)}
|  | (Refer Section B) | [10 empty] | 1000 |  |  |  |  | (Refer Section C) | [7 empty] | 1000
|  | Strip run around Substation | [9 empty] | 42.5 |  |  | sq.m |  |  | Strip run over Plant | [6 empty] | 384.2 |  |  | sq.m
|  | Total Area covered by earth strip in Plant & Substation | [13 empty] | 426.7 |  |  | sq.m
Therefore, the total surface area covered by earth grid is more than the required area of earth elements to dissipate 65kA fault current
for the 0.5sec duration as calculated above in 4.
[22 empty] | Page | 7 |  | of |  | 9

## Sheet 5
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [25 empty] | Email: contact@flasysdesign.com
D. | System Resistance:
|  | Resistance of one electrode: | [8 empty] | 9.7745 |  |  | ohm
|  | No. of electrodes forming Grid: | [8 empty] | 60
|  | Effective Resistance achieved: | [6 empty] | Re = |  | 0.16291 |  |  | ohm
E. | Grid Resistance
| Substation | [14 empty] | Plant
| Resistance of strip electrode (ref. 9.2.3 of IS: 3043_Amend 2) | [14 empty] | Resistance of strip electrode (ref. 9.2.3 of IS: 3043_Amend 2)
| Rs | = | [100p/2pi*l] x [loge(4l/t)] | [12 empty] | Rs | = | [100p/2pi*l] x [loge(4l/t)]
| where, | [14 empty] | where,
| r | = | 45 |  |  | resistivity of soil in ohm-metre | [9 empty] | r | = | 45 |  |  | resistivity of soil in ohm-metre
| l | = | 25000 |  |  | length of strip in cm | [9 empty] | l | = | 226000 |  |  | length of strip in cm
| w | = | 60 |  |  | depth of burial of the electrode in cm | [9 empty] | w | = | 60 |  |  | depth of burial of the electrode in cm
| t | = | 7.5 |  |  | width of strip in cm | [9 empty] | t | = | 7.5 |  |  | width of strip in cm
| Rs |  | 0.2721 |  |  | ohm | [9 empty] | Rs |  | 0.037076 |  |  | ohm
| Hence, Effective resistance of Substation & Plant Earth Strip, | [13 empty] | = | Substation Strip Rs x Plant Strip Rs
Substation Strip Rs + Plant Strip Rs
[15 empty] | = | 0.03263 |  |  |  | Ohm
| Effective Plant Earth Resistance | [7 empty] | = | Electrodes Re x Strip Rs
Electrodes Re x Strip Rs
[9 empty] | = |  | 0.027185 |  |  | Ohm
| 6 | Conclusion:
The effective resistance of the grounding system is 0.03 ohm, which is within the maximum permissible value of 1 ohm.
| 7 | Recommendations:
| 1. Provide min. |  |  |  | 60 |  | nos. | 3 |  |  | m. Long, |  | 100 |  |  | NB Class 'B' GI, pipe electrodes Distributed around substation & Plant
2. Each Transformer shall have 2 Nos. dedicated earth pits for Neutral grounding.
| 3. Provide GI Earth strip for main earth grid | [9 empty] | 75 x 10 |  | mm bare strip | [5 empty] | … installed at 600mm depth around Substation
| 4. Provide GI Earth strip for plant earth grid | [9 empty] | 75 x 10 |  | mm bare strip | [5 empty] | … installed at 600mm depth in plant area
5. Plant earth grid shall be connected to substation earth grid at Minimum two locations.
6. Further, this plant earth grid shall be connected to earth grids of the adjacent areas surrounding to plant at Minimum two locations.
7. Size of Earth conductors for various equipments shall be as given in the table below (referred from electrical standard installation dwg):
|  |  |  | Type of Equipment | [15 empty] | Bare GI Strip / AL or Cu cable
|  | 1. Motors above 2.2kW up to and including 30 kW | [9 empty] | (Refer E12-048) | [7 empty] | 1C x 35 sqmm AL, PVC Cable |  |  |  |  | 2 Nos.
|  | 2. Motors from 37 kW and above including MV motors | [9 empty] | (Refer E12-048) | [7 empty] | 1C x 70 sqmm AL, PVC Cable |  |  |  |  | 2 Nos.
|  | 3. HV / MV / LV switchgear, Main earth grid around substation, Plant earth grid | [17 empty] | 75 x 10 mm GI strip
|  | 4. NGR Earth Terminal | [9 empty] | (Refer E12-041) | [7 empty] | 75 x 10 mm GI strip |  |  |  |  | 2 Nos.
|  | 5. Distribution Transformer Neutral | [9 empty] | (Refer E12-040) | [7 empty] | 75 x 10 mm GI strip |  |  |  |  | 2 Nos.
|  | 6. Power & Distribution Transformer Body | [9 empty] | (Refer E12-040 / 041) | [7 empty] | 75 x 10 mm GI strip |  |  |  |  | 2 Nos.
|  | 7. Transformer HV Terminal Box | [9 empty] | (Refer E12-040 / 041) | [7 empty] | 75 x 10 mm GI strip |  |  |  |  | 2 Nos.
|  | 8. Transformer LV Terminal Box | [9 empty] | (Refer E12-040) | [7 empty] | 1C x 70 sqmm AL, PVC Cable |  |  |  |  | 2 Nos.
Contd on next sheet…
[22 empty] | Page | 8 | of | 9

## Sheet 6
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [14 empty] | Email: contact@flasysdesign.com
|  |  |  | Type of Equipment |  |  | Bare GI Strip / GI Wire
Contd from previous sheet…
|  | 8. Local Control stations (LCS) ** |  |  |  |  | 1C x 6 sqmm Cu, PVC Cable | [5 empty] | 1 No.
|  | 9. Rectifier / battery charger, Local Panels |  |  |  |  | 1C x 35 sqmm AL, PVC Cable | [5 empty] | 2 Nos.
|  | 10. Lighting Transformers |  |  |  |  | 50 x 6 mm GI strip | [5 empty] | 2 Nos.
|  | 11. Lighting, Small Power and Instrument panels, UPS |  |  |  |  | 1C x 70 sqmm AL, PVC Cable | [5 empty] | 2 Nos.
|  | 12. Street lighting poles |  |  | (Refer E12-012) |  | 1C x 35 sqmm AL, PVC Cable | [5 empty] | 2 Nos.
|  | 13. Pipe racks & cable Trays on Piperack |  |  | (Refer E12-042) |  | 50 x 6 mm GI strip at min 30 m interval | [6 empty] | 1 No.
|  | 14. Bonding of pipeworks |  |  | (Refer E12-047) |  | 1C x 35 sqmm AL, PVC Cable | [5 empty] | 1 No.
(For pipelines entering & leaving hazardous area)
|  | 15. Building columns / Steel Structure |  |  |  |  | 50 x 6 mm GI strip at min 30 m interval
|  | 16. Storage tanks (vertical and horizontal) |  |  |  |  | 50 x 6 mm GI strip | [5 empty] | 2 Nos.
|  | 17. Stairs & Ladders |  |  | (Refer E12-046) |  | 1C x 35 sqmm AL, PVC Cable | [5 empty] | 1 No.
|  | 18. Vessels and heat exchangers |  |  | (Refer E12-042) |  | 1C x 35 sqmm AL, PVC Cable | [5 empty] | 2 Nos.
|  | 19. Small equipment and instruments |  |  |  |  | 1C x 16 sqmm AL, PVC Cable | [5 empty] | 1 No.
|  | 20. | Instrument reference earth Bus (Insulated earth bus) |  |  | (Refer E12-044) | 1C x 70 sqmm AL, PVC Cable from Earth pit to
earth Bus & 1C x 6 sqmm Cu, PVC Cable from
Earth Bus to equipment
|  | 21. Horizontal Air Termination for lightning protection of buildings |  |  |  |  | 50 x 6 mm GI Strip |  |  |  | (mesh of 20 m x 10 m)
|  | 22. Down conductor for lightning protection of buildings ## |  |  |  |  | 50 x 6 mm GI Strip |  |  |  | (Qty As calculated)
|  | 23. Power JBs |  |  |  |  | 1C x 35 sqmm AL, PVC Cable | [5 empty] | 2 Nos.
|  | 24. Motors up to and including 2.2 kW $$ |  |  |  |  | 1C x 6 sqmm Cu, PVC Cable | [5 empty] | 2 Nos.
** Based on mail dated 10th Feb 2014
## Based on mail dated 20th May 2014
$$ based on confirmation to TQ-0077 dated 07th July 2014
Summary of Earth Electrodes
| 1. | Earth Pits for 4 Nos Power Transformers Neutral Earthing | [5 empty] | : | 8 | Nos
| 2. | Earth Pits for 8 Nos Distribution Transformers Neutral Earthing | [5 empty] | : | 16 | Nos
| 3. | Earth pits along the piperack (Approx. every 30m) | [5 empty] | : | 30 | Nos
| 4. | Earth pits inside plant | [5 empty] | : | 27 | Nos
| 5. | Earth Pits for Instrument Clean Earthing - Near Substation Treated Earthpits (Refer E12-38) | [5 empty] | : | 3 | Nos
| 6. | Earth Pits for Instrument Clean Earthing - Near PIB Treated Earthpits (Refer E12-38) | [5 empty] | : | 3 | Nos
| 7. | Earth Pits for Instrument Clean Earthing - in Reaction Area Treated Earthpits (Refer E12-38) | [5 empty] | : | 3 | Nos
| 8. | Earth Pits for Instrument Clean Earthing - in Elutriator Area Treated Earthpits (Refer E12-38) | [5 empty] | : | 3 | Nos
| 9. | Earth Pits for Lightning Protection System (Various structures as calculated in Section-2) | [5 empty] | : | 26 | Nos
Note : For actual location of earth electrodes refer Overall Plot Plan (ISBL) Earthing layout Dwg No. 10013-E61-CHC501-000001.
[9 empty] | Page |  | 9 | of |  | 9

## Sheet 7
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [11 empty] | Email: contact@flasysdesign.com
Section-2 : Lightning Study
| 1 | Scope:
This document covers the calculation to determine and establish the adequecy of Llightning Protection System (LPS) requirements
(for the Tall structures, Substation, PIB building & Maintenance building) .
| 2 | Reference Documents:
1. IS 2309 : Protection of Buildings and Allied Structures Against Lightning - Code of Practice
2. Doc No. 10013-P50-CHC501-001-REV-3 : Unit Plot plan
| 3 | Design Inputs:
|  | 1. No. of thunderstorm days per year = 6 |  |  |  |  | (Ref Fig. 1 of IS 2309)
|  | 2. Number of flashes to ground per sq.km per year = 0.5 |  |  |  |  | (Ref section 8.1.2 of IS 2309)
3. Earth resistance: 10 Ω for lightning
4. Down comer size 32x6 mm GI strip
Lightning Protection System (LPS)- General
The principal components of Lightning Protection System are:
a. Air terminations (e.g. rods, horizontal roof conductors, metallic roofs, hand rails etc) b. Down conductors (e.g. metal strips, part of building metal frame work, interconnected steel frame work of structure etc) c. Earth termination network/electrode (e.g. main earthing grid & earth electrodes)
Lightning Protection System - Plant
From lightning protection point of view, buildings / process units of the Plant can be broadly classified in two categories viz.
a. RCC Buildings (e.g. Substations, PIB building & Maintenance building).
b. Metallic structures/buildings (e.g. Resin Degassing & Pelletising Building, Reaction Area (including Compressor shed), Seed Bed Silos, Pellet Blending Silos, Vent Gas Recovery & Compression and Purification )
| 4 | Formulae:
1. Total Collection Area (in m2) (Ref.equation 1 of 8.1.2 of IS-2309-1989)
|  |  | Ac | =
|  |  | where, |  | Ac = Collection Area in m2
L = Length of the structure in meter
W = Width of the structure in meter
H = Height of the structure in meter
2. The probable no. of strikes (Risk) to the structure per year (Ref.equation 2 of 8.1.2 of IS-2309-1989)
|  |  | P | =
|  |  | where, |  | P = The probable no. of strikes (Risk) to the structure per year
Ac = Collection Area in m2
Ng = Lightning flashes per sq. Kilometer per year
3. Recommended No. of Down Conductors (Ref.12.2.3 of IS-2309)
For a structure having a base area exceeding 100 sq.meter , the number of Down conductors should be at least
the smaller of the following:
|  | a) | One plus an additional one for each 300 sq.meter, or a part thereof , in excess of the first 100 sq.meter.
|  | b) | One for each 30 meter of perimeter of the structure protected.
[8 empty] | Page | 1 | of | 7

## Sheet 8
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [24 empty] | Email: contact@flasysdesign.com
| 5 | Calculations:
| A. | Determination of requirement of lightning protection for substation building
Determination of “Ng” ( Lightning flash density ) :
The lightning flash density “Ng” is the number of flashes to ground per sq.km per year.
|  | Ng = |  | 0.5
Determination of “Ac” ( Effective collection area of structure ):
The effective collection area of structure is the area of the plan of the structure extended in all direction to take account of its height.
Substation Dimensions : Length (L) = 78 m, Width (W) = 18 m, Height (H) = 11 m
|  | Ac = (L x W) + 2(L x H) + 2(W x H) + (Π x H2 ) | [12 empty] | (Refer IS 2309, Figure 2)
Ac = (78 x 18) + 2(78 x 11) + 2(18 x 11) + (3.14 x 112 )
|  | Ac = |  | 3896.1327 |  |  | m2
Calculation of “Probable number of strikers”:
|  | P = Ac x Ng x 10-6 | [8 empty] | (Ref section 8.1.2 of IS 2309)
P = 3896.1 x 0.5 x 10-6
|  | P = | 0.0019481 |  |  |  | = 1.95 x 10 -3
Calculation of “Overall weighting Factors” :
Overall weigthing factors = A x B x C x D x E
= 0.7 x 0.4 x 0.8 x 1 x 0.3 ( Ref. IS 2309, Table 1 )
[8 empty] | = | 0.0672
· Determination of “Overall Risk Factor”
Overall Risk Factor = P x Overall weigthing Factor
[5 empty] | = | 0.0019481 |  |  | x | 0.0672
[5 empty] | = | 0.00013091 | [5 empty] | = 13.1 x 10 -5
[6 empty] | 13.1 x 10-5 |  |  |  | > | 10-5
As per IS 2309 Clause 8.1.3 If Overall Risk Factor is greater than 10-5, protection is required.
Air termination (mesh of 20 m x 10 m) GI strip of size 50 x 6 mm may be employed as shown in typical arrangement fig 5 of IS 2309
Calculation for number of Down conductors required :
As per Clause 12.2.3 and 12.2.4 & Tabel - 4 of IS 2309, Down conductors required shall be as follows:
Base Area of Substation building = (Area of Switchgear room ) + (Area of VFD & maint room) + (Area of Staircases)
|  |  |  | Base Area of Substation building = (78 x 12) + (6 x 24) + 3 x (6 x 6) | [13 empty] | 1188 |  | m2 | > 100 m2
Number of down conductors shall be at least the smaller of the following,
i) One + Additional one for each 300 m2 of base area in excess of first 100 m2
|  |  |  | Number of down conductors | [7 empty] | = 1 + (1188 - 100) |  | = | 4.6267 |  | ~ 5
300
ii) one for each 30 m of perimeter of structure,
[6 empty] | Perimeter of Substation building = 2 x (78 + 12) + (8 x 6) = | [9 empty] | 228 |  |  | m
[5 empty] | Number of down conductors = | [7 empty] | 228 | = | 7.6 |  | ~ 8
30
Hence 5 numbers down conductors of GI earth strip size 50 x 6 mm are required. Down conductors shall be further
connected to dedicated earth pits (5 nos).
[20 empty] | Page |  | 2 | of | 7

## Sheet 9
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [20 empty] | Email: contact@flasysdesign.com
| B. | Determination of lightning protection for Plant Interface Building (PIB)
Determination of “Ng” ( Lightning flash density ) :
The lightning flash density “Ng” is the number of flashes to ground per sq.km per year.
|  | Ng = |  | 0.5 | [5 empty] | (Ref section 8.1.2 of IS 2309)
Determination of “Ac” ( Effective collection area of structure ):
The effective collection area of structure is the area of the plan of the structure extended in all direction to take account of its height.
PIB Building Dimensions : Length (L) = 37 m, Width (W) = 10 m, Height (H) = 5.65 m
|  | Ac = (L x W) + 2(L x H) + 2(W x H) + (Π x H2 ) | [12 empty] | (Refer IS 2309, Figure 2)
Ac = (37 x 10) + 2(37 x 5.65) + 2(10 x 5.65) + (3.14 x 5.652 )
|  | Ac = |  | 1001.3367 |  | m2
Calculation of “Probable number of strikers”:
|  | P = Ac x Ng x 10-6 | [7 empty] | (Ref section 8.1.2 of IS 2309)
P = 1001.34 x 0.5 x 10-6
|  | P = | 0.00050067 |  |  | = 0.5 x 10 -3
Calculation of “Overall weighting Factors” :
Overall weigthing factors = A x B x C x D x E
= 0.7 x 0.4 x 0.8 x 1 x 0.3 ( Ref. IS 2309, Table 1 )
[7 empty] | = | 0.0672
· Determination of “Overall Risk Factor”
Overall Risk Factor = P x Overall weigthing Factor
|  |  |  | = | 0.00050067 |  | x | 0.0672
|  |  |  | = | 3.3645e-05 |  |  | = 3.4 x 10 -5
|  |  |  | = | 3.4 x 10-5 |  |  | > | 10-5
As per IS 2309 Clause 8.1.3 If Overall Risk Factor is greater than 10-5, protection is required.
Air termination (mesh of 20 m x 10 m) GI strip of size 50 x 6 mm may be employed as shown in typical arrangement fig 5 of IS 2309
Calculation for number of Down conductors required :
As per Clause 12.2.3 and 12.2.4 & Tabel - 4 of IS 2309, Down conductors required shall be as follows:
Base Area of PIB building = 37 x 10 = 370 m2 > 100 m2
Number of down conductors shall be at least the smaller of the following,
i) One + Additional one for each 300 m2 of base area in excess of first 100 m2
|  |  | Number of down conductors | [5 empty] | = 1 + (370 - 100) |  |  | = | 1.9 |  | ~ 2 | [6 empty] | .
300
ii) one for each 30 m of perimeter of structure,
[5 empty] | Perimeter of PIB building = (2 x 30) + (2 x 10) = | [7 empty] | 80
|  |  |  | Number of down conductors = | [6 empty] | 80 |  | = | 2.6667 |  | ~ 3
30
Hence 2 numbers down conductors of GI earth strip size 50 x 6 mm are required. Down conductors shall be further
connected to dedicated earth pits (2 nos).
[17 empty] | Page | 3 | of | 7

## Sheet 10
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [20 empty] | Email: contact@flasysdesign.com
| C. | Determination of lightning protection for Maintenance Building
Determination of “Ng” ( Lightning flash density ) :
The lightning flash density “Ng” is the number of flashes to ground per sq.km per year.
|  | Ng = |  | 0.5 | [5 empty] | (Ref section 8.1.2 of IS 2309)
Determination of “Ac” ( Effective collection area of structure ):
The effective collection area of structure is the area of the plan of the structure extended in all direction to take account of its height.
Maintenance Building Dimensions : Length (L) = 34.5 m, Width (W) = 23.50 m, Height (H) = 7.7 m
|  | Ac = (L x W) + 2(L x H) + 2(W x H) + (Π x H2 ) | [12 empty] | (Refer IS 2309, Figure 2)
Ac = (34.5 x 23.5) + 2(34.5 x 7.7) + 2(23.5 x 7.7) + (3.14 x 7.72 )
|  | Ac = |  | 1890.1206 |  | m2
Calculation of “Probable number of strikers”:
|  | P = Ac x Ng x 10-6 | [7 empty] | (Ref section 8.1.2 of IS 2309)
P = 1890.12 x 0.5 x 10-6
|  | P = | 0.00094506 |  |  | = 0.95 x 10 -3
Calculation of “Overall weighting Factors” :
Overall weigthing factors = A x B x C x D x E
= 0.7 x 0.4 x 0.8 x 1 x 0.3 ( Ref. IS 2309, Table 1 )
[7 empty] | = | 0.0672
· Determination of “Overall Risk Factor”
Overall Risk Factor = P x Overall weigthing Factor
|  |  |  | = | 0.00094506 |  | x | 0.0672
|  |  |  | = | 6.3508e-05 |  |  | = 6.4 x 10 -5
|  |  |  | = | 6.4 x 10-5 |  |  | > | 10-5
As per IS 2309 Clause 8.1.3 If Overall Risk Factor is greater than 10-5, protection is required.
Air termination (mesh of 20 m x 10 m) GI strip of size 50 x 6 mm may be employed as shown in typical arrangement fig 6 of IS 2309
Calculation for number of Down conductors required :
As per Clause 12.2.3 and 12.2.4 & Tabel - 4 of IS 2309, Down conductors required shall be as follows:
Base Area of the building = 34.5 x 23.5 = 810.75 m2 > 100 m2
Number of down conductors shall be at least the smaller of the following,
i) One + Additional one for each 300 m2 of base area in excess of first 100 m2
|  |  | Number of down conductors | [5 empty] | = 1 + (810.7 - 100) |  |  | = | 3.3692 |  | ~ 4 | [6 empty] | .
300
ii) one for each 30 m of perimeter of structure,
[5 empty] | Perimeter of the building = (2 x 34.5) + (2 x 23.5) = | [7 empty] | 116
|  |  |  | Number of down conductors = | [6 empty] | 116 |  | = | 3.8667 |  | ~ 4
30
Hence 4 numbers down conductors of GI earth strip size 50 x 6 mm are required. Down conductors shall be further
connected to dedicated earth pits (4 nos).
[17 empty] | Page | 4 | of | 7

## Sheet 11
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [20 empty] | Email: contact@flasysdesign.com
| D. | Determination of lightning protection for Catalyst Storage Building
Determination of “Ng” ( Lightning flash density ) :
The lightning flash density “Ng” is the number of flashes to ground per sq.km per year.
|  | Ng = |  | 0.5 | [5 empty] | (Ref section 8.1.2 of IS 2309)
Determination of “Ac” ( Effective collection area of structure ):
The effective collection area of structure is the area of the plan of the structure extended in all direction to take account of its height.
Catalyst storage Building Dimensions : Length (L) = 40 m, Width (W) = 40 m, Height (H) = 8.7 m
|  | Ac = (L x W) + 2(L x H) + 2(W x H) + (Π x H2 ) | [12 empty] | (Refer IS 2309, Figure 2)
Ac = (40 x 40) + 2(40 x 8.7) + 2(40 x 8.7) + (3.14 x 8.72 )
|  | Ac = |  | 3229.6666 |  | m2
Calculation of “Probable number of strikers”:
|  | P = Ac x Ng x 10-6 | [7 empty] | (Ref section 8.1.2 of IS 2309)
P = 3229.67 x 0.5 x 10-6
|  | P = | 0.0016148 |  |  | = 1.61 x 10 -3
Calculation of “Overall weighting Factors” :
Overall weigthing factors = A x B x C x D x E
= 0.7 x 0.4 x 0.8 x 1 x 0.3 ( Ref. IS 2309, Table 1 )
[7 empty] | = | 0.0672
· Determination of “Overall Risk Factor”
Overall Risk Factor = P x Overall weigthing Factor
|  |  |  | = | 0.0016148 |  | x | 0.0672
|  |  |  | = | 0.00010852 |  |  | = 10.9 x 10 -5
|  |  |  | = | 10.9 x 10-5 |  |  | > | 10-5
As per IS 2309 Clause 8.1.3 If Overall Risk Factor is greater than 10-5, protection is required.
Air termination (mesh of 20 m x 10 m) GI strip of size 50 x 6 mm may be employed as shown in typical arrangement fig 6 of IS 2309
Calculation for number of Down conductors required :
As per Clause 12.2.3 and 12.2.4 & Tabel - 4 of IS 2309, Down conductors required shall be as follows:
Base Area of the building = 40 x 40 = 1600 m2 > 100 m2
Number of down conductors shall be at least the smaller of the following,
i) One + Additional one for each 300 m2 of base area in excess of first 100 m2
|  |  | Number of down conductors | [5 empty] | = 1 + (1600 - 100) |  |  | = | 6 | [8 empty] | .
300
ii) one for each 30 m of perimeter of structure,
[5 empty] | Perimeter of the building = (2 x 40) + (2 x 40) = | [7 empty] | 160
|  |  |  | Number of down conductors = | [6 empty] | 160 |  | = | 5.3333 |  | ~ 6
30
Hence 6 numbers down conductors of GI earth strip size 50 x 6 mm are required. Down conductors shall be further
connected to dedicated earth pits (6 nos).
[17 empty] | Page | 5 | of | 7

## Sheet 12
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [17 empty] | Email: contact@flasysdesign.com
E. | LPS FOR METALLIC STRUCTURES / BUILDINGS
a. | Resin Degassing & Pelletising Building:
| Area of the Structure : 50.3 Mtr. x 45.5 Mtr. | [5 empty] | (Base Area)
Height of the Structure : 133.7 Mtr.
Resin Degassing & Pelletising is having Concrete Structure upto EL 69.8 m and metallic structures above (made of structural steel columns, beams, interconnecting framework, platforms at different elevations, handrails etc.). Since the total structure is metallic and firmly bonded from top to bottom they can be considered as “Natural components” of LPS. Hence no separate “Air Termination Network” and “Down Conductors” are envisaged for Structure above EL 69.8 m Peripheral steel columns of these structures shall be connected (at every 30 Mtrs interval) to main Earthing Network via 50 x 6 mm GI strips,
However Lightning Protection for the Concrete structure (terrace) at EL 63.300 & EL 69.800 shall be provided.
Air termination (mesh of 20 m x 10 m) GI strip of size 50 x 6 mm may be employed as shown in typical arrangement fig 5 of IS 2309
Since the Structure is above 20 m Height, calculation for Probable no. of strikes & Risk factor is omitted.
And it is considered that Lightning protection is required.
Calculation for number of Down conductors required :
As per Clause 12.2.3 and 12.2.4 & Tabel - 4 of IS 2309, Down conductors required shall be as follows:
Base Area of Structure = 50.3 x 45.5 = 2288.65 m2 > 100 m2
Number of down conductors shall be at least the smaller of the following,
i) One + Additional one for each 300 m2 of base area in excess of first 100 m2
|  |  | Number of down conductors |  |  | = 1 + (2288.65 - 100) |  |  | = | 8.2955 |  | ~ 9 | [6 empty] | .
300
ii) one for each 30 m of perimeter of structure,
[5 empty] | Perimeter of Structure = (2 x 50.3) + (2 x 45.5) = |  |  |  |  | 191.6
|  |  |  | Number of down conductors = |  |  |  | 191.6 |  | = | 6.3867 |  | ~ 7
30
Hence 7 Nos numbers down conductors of GI earth strip size 50 x 6 mm are required for the Lightning protection Grid.
Additionally 2 Nos Down conductors are required for Direct connection of Steel structure (above EL 69.8 m) to the Earth grid.
Therefore Total 9 Nos Down conductors shall be required to be connected to dedicated earth pits (9 nos).
b. | Other Structures in the Plant (having Height above 20 m)
Most of the process units in the plant are metallic structures (made of structural steel columns, beams, interconnecting framework, platforms at different elevations, handrails etc.) Since these structures are metallic and firmly bonded from top to bottom they can be considered as “Natural components” of LPS and hence no separate “Air Termination Network” and “Down Conductors” are necessary. (Refer sections 12.1, 12.2 & 12.5.3 of IS 2309:1989)
Peripheral steel columns of these structures shall be connected (at every 30 Mtrs interval) to main Earthing Network via 50 x 6 mm GI strips. Resistance to earth for LPS shall be less than 10 Ω. (Refer IS 2309: 1989 section 12.3.1).
Since earth termination network of LPS and plant main earth network is common (as recommended in IS 2309:1989 section 12.3.3) the resistance to earth shall be less than 1 Ω thus ensuring very efficient LPS.
Below is the list of such structures
i. | Reaction Area (including Compressor shed)
Area of the Structure : 66 Mtr. x 31.5 Mtr.
Height of the Structure : 83.85 Mtr.
[14 empty] | Page | 6 | of | 7

## Sheet 13
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation |  | Email: contact@flasysdesign.com
ii. | Seed Bed Silos
Area of the Structure : 30.25 Mtr. x 8.5 Mtr.
Height of the Structure : 81.5 Mtr.
iii. | Pellet Blending Silos
Area of the Structure : 94.65 Mtr. x 11 Mtr.
Height of the Structure : 79.5 Mtr.
iv. | Vent Gas Recovery & Compression
VGR Structure
Area of the Structure : 34 Mtr. x 25 Mtr.
Height of the Structure : 59.15 Mtr.
Compressor shed
Area of the Structure : 42 Mtr. x 21 Mtr.
Height of the Structure : 50.7 Mtr.
v. | Purification
Hexene & Butene Area
Area of the Structure : 36 Mtr. x 8 Mtr. + 12 Mtr. x 12 Mtr.
Height of the Structure : 63.2 Mtr.
Hydrogen Compressor Area
Area of the Structure : 33.5 Mtr. x 7 Mtr.
Height of the Structure : 52.5 Mtr.
Nitrogen Compressor Area
Area of the Structure : 30 Mtr. x 7 Mtr.
Height of the Structure : 47.65 Mtr.
ICA & Butane Area
Area of the Structure : 24 Mtr. x 8 Mtr. + 12 Mtr. x 12 Mtr.
Height of the Structure : 53 Mtr.
Ethylene Area
Area of the Structure : 59 Mtr. x 8 Mtr.
Height of the Structure : 57.8 Mtr.
Hydrogen compressor Shed
Area of the Structure : 11 Mtr. x 14 Mtr.
Height of the Structure : 9 Mtr.
Note: Although the structure height is less than 20m, due to potential hazard of Hydrogen gas
the structure is provided with 2 nos Lightning protection earth pits.
v. | Piperack PR-12
Grid PR/18 to PR/96 of this piperack is having height Approx 23 m. Further this piperack is located between C&P Building & Reaction structure
Which are covered in lightning protection calculation above. Therefore separate lightning protection is not required for piperack PR-12,
However for additional safety 2 nos of Lightning Earth pits are considered for Lightning protection
6 | SUMMARY
(a) | For this Plant, LPS for RCC buildings has been determined as per IS-2309:1989 guidelines.
(b) | For all process units which are metallic structures, no separate “Air Termination Network” and “Down Conductors” are proposed/provided. This is in line with IS recommendations. At ground level, these structures are connected to “Main Earth Network” to ensure earth connectivity below 1 Ω.
|  |  | Page | 7 | of | 7

## Annex-1
https://www.flasysdesign.com/
Earthing & Lightning Protection Calculation | [18 empty] | Email: contact@flasysdesign.com
Annexure-1
| 1. | Fault current calculations for 415V Motor
Largest LV Motor on 415V Switchboard in the plant is SEED BED BLOWER MOTOR (Tag no. MA-CHC501-M5613, 5614) of rating 225 kW.
The fault current calculated at this motor terminal is as below :
|  | Fault current available at PMCC Bus | [5 empty] | 65 |  | kA
|  | Source Voltage | [5 empty] | 0.415 |  | kV
|  | Source Reactance (Xs) | [5 empty] | 0.0036863 |  | Ohm
|  | Cable size used | [5 empty] | 3C X 300 |  | sqmm Aluminium cable |  |  |  | (Selected based on LV cable sizing table 10080-1-ENGG-GUI-EL-003)
|  | No of runs | [5 empty] | 3
|  | Cable Length | [5 empty] | 275 |  | m |  |  |  | (Estimated from plot plan)
|  | Cable Resistance |  |  | (ohm/km) |  |  | 0.128 |  | ohm/km
|  | Cable Reactance |  |  | (ohm/km) |  |  | 0.0705 |  | ohm/km
|  | Actual Cable Resistance |  |  |  | Rc |  | 0.011733 |  | ohm
|  | Actual Cable Reactance |  |  |  | Xc |  | 0.0064625 |  | ohm
|  | Z total = | Ö | Rc2 + (Xs + Xc)2 |  | Z total |  | 0.015513 |  | ohm
|  | Fault current at end of Cable | [5 empty] | 15.4451 |  | kA
| 2. | Fault current calculations for 690V Motor
From substation nearest 690V Motor in the plant is PELLET WATER PUMP MOTOR (Tag no. MP-CHC501-M7012 / 7017) of rating 250kW.
The fault current calculated at this motor terminal is as below :
|  | Fault current available at PMCC Bus | [5 empty] | 65 |  | kA
|  | Source Voltage | [5 empty] | 0.69 |  | kV
|  | Source Reactance (Xs) | [5 empty] | 0.006129 |  | Ohm
|  | Cable size used | [5 empty] | 3C X 150 |  | sqmm Aluminium cable |  |  |  | (Selected as per LV cable sizing calculation 10013-EWLC-CHC501-002)
|  | No of runs | [5 empty] | 2
|  | Cable Length | [5 empty] | 190 |  | m
|  | Cable Resistance |  |  | (ohm/km) |  |  | 0.264 |  | ohm/km
|  | Cable Reactance |  |  | (ohm/km) |  |  | 0.0716 |  | ohm/km
|  | Actual Cable Resistance |  |  |  | Rc |  | 0.02508 |  | ohm
|  | Actual Cable Reactance |  |  |  | Xc |  | 0.006802 |  | ohm
|  | Z total = | Ö | Rc2 + (Xs + Xc)2 |  | Z total |  | 0.028217 |  | ohm
|  | Fault current at end of Cable | [5 empty] | 14.1184 |  | kA
| Since calculated fault current for 415V system | [6 empty] | 15.4451 | kA is more than |  |  | 14.1184 | kA calculated for 690V system. Maximum fault
| current for Plant earth strip sizing shall be considered as | [8 empty] | 15.4451 | kA
[15 empty] | Page | 1 | of | 1

## Portrait Page (hidden)
J3 Program
Specification for …….
Doc. No. 10013-EGC-CHC501-001 | Page
Rev: 0

## Earth Pit Count (hidden)
Earth Pit Count
60 | Substation & Plant Eartrh Grid including Transformer Neutral Grounding Pits
6 | Instrument Clean earthing
66 | Total EP
Lightning Earth Pits
5 | substation building
3 | Plant Interface Building (PIB)
3 | Maintenance Building
11 | Total LEP
77 | Total EP + LEP