## HT Cable
HT Cable Sizing Calculation | [9 empty] | https://www.flasysdesign.com/
Email: contact@flasysdesign.com
Input Data
| Voltage |  |  | = | 11 | KV
| Load Rating |  |  | = | 1500 | KVA
| Full load Current |  |  | = | 78.7319 | Amps
| IK - Short Cicuit Current in KA |  |  | = | 20 | KA
| Duration of Short Circuit Current |  |  | = | 1 | Sec | As per IS: 3043, Pg.No-31
| K - Conductor connstant |  |  | = | 94 |  | K - Factor | Copper | Aluminium
| A - Area of conductor Size |  |  | = | ? |  | XLPE Cables | 143 | 94
[7 empty] | PVC Cables | 115 | 76
Calculation
| Area of Aluminium cable |  |  | = | I x √t
K
|  |  |  | = | 20 | x | 1
94
|  |  |  | = | 212.766
| Area of aluminium conductor is |  |  | = | 1 x | 240 | Sq.mm | (total 240 Sq.mm)
Cable Data
| 1. Rating factor for variation in ground temperature at 45⁰ C |  |  |  |  | = | 0.87
| 2. Rating factor of cable for laying arrangement |  |  |  |  | = | 0.99
| 3. Rating factor for variation in thermal resistivity of soil at 150⁰ C |  |  |  |  | = | 1
| 4. Rating factor for cable laid in ground in horizondal formation in 2 cable @ 45mm distance |  |  |  |  | = | 0.9
| 3. No of Runs |  |  |  |  | = | 1
| Cable Current Rating for | 240 | Sq.mm |  |  | = | 355 | A
Derating Factor Calculation
| Total Derating factor |  |  | = | (1) x (2) x (3) x (4)
|  |  |  | = | 0.77517
| Derated Current for cable |  |  | = | 355 | x | 0.77517 | x | 1
| After Derating Cable current is |  |  | = | 275.1854 | Amps
Therefore The derated Current is more then the Full load Current, So The Selected Cable is Sufficient to carry the Load
Cable Data
| Resistance (ohm/Km) |  |  | R |  |  | = | 0.13
| Reactance @50Hz |  |  | X |  |  | = | 0.103
| Operating P.F. |  |  | cos Φ |  |  | = | 0.8
| Actual.Length (Meters) | [5 empty] | = | 250
| Maximum AllowableLength (M) | [5 empty] | = | 500
Voltage Drop Calculation
| Impedence (ohm/km) |  |  | R cos f + X sin f |  |  | = | 0.1658
| Required Number of Runs | [5 empty] | = | 1
| Impedence when laid parallel | Impedence/ No of Runs |  |  |  |  | = | 0.1658
| Calculated Voltage Drop |  |  |  |  | 1.732x I x Impedx Length/ 1000 | = | 5.6523
| Calculated % Voltage Drop |  |  |  |  | Cal Voltage drop/Sys Voltagex 100 | = | 0.05138%
| Allowable % Voltage Drop | [5 empty] | = | 2.5%
Note:
Voltage drop at the cable between the HT SWGR to HT SWGR shall be limited to 2.5% as per standard practice.
CABLE SIZE IS OK
The Final Cable Size is 1R x 3C x 240 Sq.mm Al XLPE
Input Data
| Voltage |  |  | = | 11 | KV
| Load Rating |  |  | = | 750 | KVA
| Full load Current |  |  | = | 39.3659 | Amps
| IK - Short Cicuit Current in KA |  |  | = | 18.5 | KA
| Duration of Short Circuit Current |  |  | = | 1 | Sec | As per IS: 3043, Pg.No-31
| K - Conductor connstant |  |  | = | 94 |  | K - Factor | Copper | Aluminium
| A - Area of conductor Size |  |  | = | ? |  | XLPE Cables | 143 | 94
[7 empty] | PVC Cables | 115 | 76
Calculation
| Area of Aluminium cable |  |  | = | I x √t
K
|  |  |  | = | 18.5 | x | 1
94
|  |  |  | = | 196.8085
| Area of aluminium conductor is |  |  | = | 1 x | 185 | Sq.mm | (total 185 Sq.mm)
Cable Data
| 1. Rating factor for variation in ground temperature at 45⁰ C |  |  |  |  | = | 0.87
| 2. Rating factor of cable for laying arrangement |  |  |  |  | = | 0.99
| 3. Rating factor for variation in thermal resistivity of soil at 150⁰ C |  |  |  |  | = | 1
| 4. Rating factor for cable laid in ground in horizondal formation in 2 cable @ 45mm distance |  |  |  |  | = | 0.9
| 3. No of Runs |  |  |  |  | = | 1
| Cable Current Rating for | 185 | Sq.mm |  |  | = | 275 | A
Derating Factor Calculation
| Total Derating factor |  |  | = | (1) x (2) x (3) x (4)
|  |  |  | = | 0.77517
| Derated Current for cable |  |  | = | 275 | x | 0.77517 | x | 1
| After Derating Cable current is |  |  | = | 213.1718 | Amps
Therefore The derated Current is more then the Full load Current, So The Selected Cable is Sufficient to carry the Load
Cable Data
| Resistance (ohm/Km) |  |  | R |  |  | = | 0.21
| Reactance @50Hz |  |  | X |  |  | = | 0.11
| Operating P.F. |  |  | cos Φ |  |  | = | 0.8
| Actual.Length (Meters) | [5 empty] | = | 350
| Maximum AllowableLength (M) | [5 empty] | = | 500
Voltage Drop Calculation
| Impedence (ohm/km) |  |  | R cos f + X sin f |  |  | = | 0.234
| Required Number of Runs | [5 empty] | = | 1
| Impedence when laid parallel | Impedence/ No of Runs |  |  |  |  | = | 0.234
| Calculated Voltage Drop |  |  |  |  | 1.732x I x Impedx Length/ 1000 | = | 5.5841
| Calculated % Voltage Drop |  |  |  |  | Cal Voltage drop/Sys Voltagex 100 | = | 0.05076%
| Allowable % Voltage Drop | [5 empty] | = | 2.5%
Note:
Voltage drop at the cable between the HT SWGR to HT SWGR shall be limited to 2.5% as per standard practice.
CABLE SIZE IS OK
The Final Cable Size is 1R x 3C x 185 Sq.mm Al XLPE
Input Data
| Voltage |  |  | = | 11 | KV
| Transformer Rating |  |  | = | 500 | KVA
| Full load Current |  |  | = | 26.244 | Amps
| IK - Short Cicuit Current in KA |  |  | = | 18.5 | KA
| Duration of Short Circuit Current |  |  | = | 0.5 | Sec | As per IS: 3043, Pg.No-31
| K - Conductor connstant |  |  | = | 94 |  | K - Factor | Copper | Aluminium
| A - Area of conductor Size |  |  | = | ? |  | XLPE Cables | 143 | 94
[7 empty] | PVC Cables | 115 | 76
Calculation
| Area of Aluminium cable |  |  | = | I x √t
K
|  |  |  | = | 18.5 | x | 0.70711
94
|  |  |  | = | 139.1646
| Area of aluminium conductor is |  |  | = | 1 x | 185 | Sq.mm | (total 480 Sq.mm)
Cable Data
| 1. Rating factor for variation in ground temperature at 45⁰ C |  |  |  |  | = | 0.87
| 2. Rating factor of cable for laying arrangement |  |  |  |  | = | 0.99
| 3. Rating factor for variation in thermal resistivity of soil at 150⁰ C |  |  |  |  | = | 1
| 4. Rating factor for cable laid in ground in horizondal formation in 2 cable @ 45mm distance |  |  |  |  | = | 0.9
| 3. No of Runs |  |  |  |  | = | 1
| Cable Current Rating for | 185 | Sq.mm |  |  | = | 275 | A
Derating Factor Calculation
| Total Derating factor |  |  | = | (1) x (2) x (3) x (4)
|  |  |  | = | 0.77517
| Derated Current for cable |  |  | = | 275 | x | 0.77517 | x | 1
| After Derating Cable current is |  |  | = | 213.1718 | Amps
Therefore The derated Current is more then the Full load Current, So The Selected Cable is Sufficient to carry the Load
Cable Data
| Resistance (ohm/Km) |  |  | R |  |  | = | 0.21
| Reactance @50Hz |  |  | X |  |  | = | 0.11
| Operating P.F. |  |  | cos Φ |  |  | = | 0.8
| Actual.Length (Meters) | [5 empty] | = | 15
| Maximum AllowableLength (M) | [5 empty] | = | 20
Voltage Drop Calculation
| Impedence (ohm/km) |  |  | R cos f + X sin f |  |  | = | 0.234
| Required Number of Runs | [5 empty] | = | 1
| Impedence when laid parallel | Impedence/ No of Runs |  |  |  |  | = | 0.234
| Calculated Voltage Drop |  |  |  |  | 1.732x I x Impedx Length/ 1000 | = | 0.15955
| Calculated % Voltage Drop |  |  |  |  | Cal Voltage drop/Sys Voltagex 100 | = | 0.00145%
| Allowable % Voltage Drop | [5 empty] | = | 2.5%
Note:
Voltage drop at the cable between the HT SWGR to HT SWGR shall be limited to 2.5% as per standard practice.
CABLE SIZE IS OK
The Final Cable Size is 1R x 3C x 185 Sq.mm Al XLPE