## Rectangular Structure
FLASYS DESIGN | [8 empty] | Rev. 0
LIGHTNING PROTECTION SYSTEM
RISK ASSESSMENT SHEET AS PER (NFPA 780)
Project Details:
Project Name:
| Project No.: |  |  |  | Building Name:
Abbreviations:
| Nd | Yearly expected lightning strike frequency to the structure
| Nc | Tolerable lightning strike frequency to the structure
| Ng | Yearly average flash density in the region (fl/km2/year)
| Ae | Equivalent collective area of the structure (km2)
| C1 | Environmental coefficient
| C2 | Structure Coefficient
| C3 | Structure Contents Coefficient
| C4 | Structure Occupancy Coefficient
| C5 | Lightning Consequence Coefficient
Building Dimensions:
| Length(L) (m): |  | 37 | Width(W) (m): |  | 60 | Height(H) (m): |  | 10.5
Collective Area Calculation (Ae):
Rectangular structure
| Ae = | LW + 6H(L+W) + π 9 H2
| Ae = | 11446.665 | m2
Determination of Location Factor (C1):
| C1 | Relative Structure Location
| 0.25 | Structure surrounded by taller structures or trees within a distance of 3H.
| 0.5 | Structure surrounded by structures of equal or lesser height within a distance of 3H.
| 1 | Isolated structure, with no other structures located within a distance of 3H.
| 2 | Isolated structure on hilltop.
| C1 = | 0.5
Determination of Average Flash Density (Ng):
Reference : http://www.nasa.gov/centers/goddard/news/topstory/2004/0621lightning_prt.htm
| Location: |  | ABU DHABI |  |  | Ng = | 10 | fl/km2/year
Calculation of Expected Lightning Strike Frequency (Nd):
| Nd = | (Ng) x (Ae) x (C1) x 10 -6
| Nd = | 0.057233 | event/year | .
Determination of Construction Coefficient (C2):
Roof Material
| Structure Material |  | Metal |  | Nonmetallic |  | Combustible
| Metal |  | 0.5 |  | 1 |  | 2
| Nonmetallic |  | 1 |  | 1 |  | 2.5
| Combustible |  | 2 |  | 2.5 |  | 3
| C2 = | 1
Determination of Structure Contents Coefficient (C3):
| C3 | Structure Contents
| 0.5 | Low value and noncombustible.
| 1 | Standard value and noncombustible.
| 2 | High value, moderate combustibility.
| 3 | Exceptional value, flammable liquids, computer or electronics.
| 4 | Exceptional value, irreplaceable cultural items.
| C3 = | 0.5
Determination of Structure Occupancy Coefficient (C4):
| C4 | Structure Occupancy
| 0.5 | Unoccupied.
| 1 | Normally Occupied.
| 3 | Difficult to evacuate or risk of panic.
| C4 = | 1
Determination of Lightning Consequence Coefficient (C5):
| C5 | Lightning Consequence
| 1 | Continuity of facility services not required, no environmental impact.
| 5 | Continuity of facility services required, no environmental impact.
| 10 | Consequences to the environment.
| C5 = | 1
Calculation of Tolerable Lightning Strike Frequency (Nc):
| Nc = | 1.5 x 10 -3
(C2)(C3)(C4)(C5)
| Nc = | 0.003 | event/year
Risk Calculation:
|  | if | Nd | ≤ | Nc | Hence, LPS May Be Optional
|  |  | Nd | > | Nc | Hence, LPS Should Be Installed
Accordingly,
Lighting Protection System ( LPS )
Should Be Installed