## Sheet3
Fault Current Calculation (Base KVA Method)
Base KVA Details:
Base KVA for H.T. Breaker and Transformer Primary |  | 6 | MVA
Base KV for H.T. Breaker and Transformer Primary |  | 6.6 | KV
Base KVA for Transformer Secondary and down stream |  | 2.5 | MVA
Base KVA for Transformer Secondary and down stream |  | 0.415 | KV
HT Incoming Power Supply Details
HT Power received at |  | 6.6 | KV
Fault Level at HT Incoming Power Supply |  | 360 | MVA
Transformer Details:
Transformer Rating |  | 2.5 | MVA
Transformer Impedence |  | 6% | 6
% Reactance at Base KVA |  | 6%
Fault Level at HT Side (Sub-station):
From | To | Cable Details | [7 empty] | Z PU Reactance | Total Impedance up to this Location (Ω) | Fault Level
|  | Cable Size | No of Run | Length (Meter) | Resistance (Ω/Km) | Reactance (Ω/Km) | Total Cable Resistance (R5) | Total Cable Reactance (X5) | Z Impedance (Ω) |  |  | Fault Level @ Locations | Fault MVA | Fault Current (KA)
HT incoming | HT Circuit Breaker |  | 5 | 50 | 0.1023 | 0.099 | 0.001023 | 0.00099 | 0.0014236 | 0.016667 | 0.01809 | HT Circuit Breaker | 331.6701 | 50.253
HT Circuit Breaker | Primary Side of Transformer |  | 3 | 400 | 0.1023 | 0.099 | 0.01364 | 0.0132 | 0.018981 | 0.0026145 | 0.020705 | Primary Side of Transformer | 289.7883 | 43.9073
Primary Side of Transformer | [10 empty] | 0.020705 |  | 289.7883 | 43.9073
[11 empty] | 0.020705 |  | 289.7883 | 43.9073
[11 empty] | 0.020705 |  | 289.7883 | 43.9073
| Secondary Side of Transfomer | [8 empty] | 0.06 | 0.080705 | Secondary Side of Transfomer | 30.9771 | 43.0968
Fault Level at LV Side (Substation to Down Stream):
Secondary Side of Transfomer | Main LT Panel |  | 13 | 12 | 0.1023 | 0.0618 | 9.4431e-05 | 5.7046e-05 | 0.00011032 | 0.0016015 | 0.082306 | Main LT Panel | 30.3744 | 42.2582
Main LT Panel | Feeder Piller |  | 2 | 160 | 0.1023 | 0.0618 | 0.008184 | 0.004944 | 0.0095614 | 0.13879 | 0.2211 | Feeder Piller | 11.3072 | 15.731
Feeder Piller | Sub Panel |  | 6 | 150 | 0.123 | 0.0739 | 0.003075 | 0.0018475 | 0.0035873 | 0.052073 | 0.27317 | Sub Panel | 9.1517 | 12.7323
Sub Panel | Motor Control Panel |  | 6 | 150 | 0.123 | 0.0739 | 0.003075 | 0.0018475 | 0.0035873 | 0.052073 | 0.32525 | Motor Control Panel | 7.6865 | 10.6938
Motor Control Panel