## S.C Current At Various Point
Calculate Short Circuit Current at Various Point of Distribution Network
Transformer Detail
System Voltage Primary (E1) : |  |  | 11 | KV
System Voltage Secondary (E2): |  |  | 415 | V
Short Circuit MVA @11 Side (Psc): |  |  | 193 | MVA
Transformer rating (P): |  |  | 1600 | KVA
Transformer %Impedance (Z): |  |  | 6.25
Transformation ratio (K): |  |  | 0.037727
SC Current withstand time (t): |  |  | 1 | Sec
Constant for PVC Aluminium cable (C): |  |  | 13.2
Constant for PVC Copper cable (C): |  |  | 8.69
Constant for XLPE Aluminium cable (C): |  |  | 10.63
Constant for XLPE Copper cables (C): |  |  | 6.99
Fault Current at Secondary of Transformer
Total Impedance of Upstream network (Zup) : |  |  | 0.62694 | Ω |  | Zup=(E1*E1) / Psc
Impedance on Low Voltage Side (Zup (low)): |  |  | 0.00089236 | Ω |  | Zup(Low)=ZupxKxK
Impedance of the transformer (Zt): |  |  | 0.0067275 | Ω |  | Zt=(E2*E2) / (P*1000)*%Z /100
Total Impedance on Transformer Low Voltage Side : |  |  | 0.0076199 | Ω
Fault Current on the Sec. of Transformer (Isc): |  |  | 31.445 | KA |  | Isc=E2 / (1.732*(Zup+Zt)
Enter Constant (C) for Cable Conductor: |  |  | 10.63
The minimum size of the conductor in Sq.mm required to withstand shortcircuit current Isc in kA for t sec |  |  | 334.26 | Sq.mm |  | S=IscxCxSqrt(t)
Fault Current at various Point of Distribution Network
Panel Detail |  | Cable Detail | [7 empty] | Fault Current at Location of |  |  | Cable Size |  | Remarks
From | To | Impedance of cable |  |  | No of Cable Runs | Cable Length (Meter) | Constant for Cable C | Z up to up stream | Total Z | Fault Current at Location of | Fault current withstand time in sec | Fault Current Ics in kA | Required Size of Cable in Sq.mm | Actual Cable Size Sq.mm
|  | R (Ω/Km) | X (Ω/Km) | Z
Transformer-1 | DG PANEL-1 | 0.000129 | 7.05e-05 | 0.0051453 | 10 | 350 | 11.1 | 0.0076199 | 0.012765 | DG PANEL-1 | 0.2 | 18.7704 | 93.1777 | 2x150 |  | DG PANEL-1 | 0.012765
DG PANEL-1 | SMSB-A&B | 0.000129 | 7.05e-05 | 0.00027564 | 8 | 15 | 11.1 | 0.012765 | 0.013041 | SMSB-A&B | 0.2 | 18.3737 | 91.2082 | 8x300 |  | SMSB-A&B | 0.013041 | 0.012765 | 0.013041
DG PANEL-1 | SMSB-C&D | 0.000129 | 7.05e-05 | 0.00027564 | 8 | 15 | 11.1 | 0.012765 | 0.013041 | SMSB-C&D | 0.2 | 18.3737 | 91.2082 | 1x300 |  | SMSB-C&D | 0.013041 | 0.012765 | 0.013041
SMSB-A&B | MLP | 0.00021 | 7.18e-05 | 0.0016645 | 2 | 15 | 11.1 | 0.013041 | 0.014705 | MLP | 0.2 | 16.2939 | 80.8842 | 2x185 |  | MLP | 0.014705 | 0.013041 | 0.014705
SMSB-C&D | AHU-1 | 0.000264 | 7.16e-05 | 0.0020515 | 2 | 15 | 11.1 | 0.013041 | 0.015092 | AHU-1 | 0.2 | 15.8761 | 78.8101 | 2x150 |  | AHU-1 | 0.015092 | 0.013041 | 0.015092
SMSB-A&B | UPS-B1 | 0.00016 | 8.39e-05 | 0.0027099 | 2 | 30 | 11.1 | 0.013041 | 0.015751 | UPS-B1 | 0.2 | 15.2124 | 75.5156 | 2x150 |  | UPS-B1 | 0.015751 | 0.013041 | 0.015751
SMSB-A&B | UPS-ACOP | 0.00016 | 8.39e-05 | 0.0027099 | 2 | 30 | 11.1 | 0.013041 | 0.015751 | UPS-ACOP | 0.2 | 15.2124 | 75.5156 | 2x150 |  | UPS-ACOP | 0.015751 | 0.013041 | 0.015751
SMSB-A&B | CAFETERIA | 0.00021 | 7.18e-05 | 0.039948 | 2 | 360 | 11.1 | 0.013041 | 0.052989 | CAFETERIA | 0.2 | 4.5218 | 22.4466 | 2x185 |  | CAFETERIA | 0.052989 | 0.013041 | 0.052989
SMSB-C&D | AHU-2 | 0.000264 | 7.16e-05 | 0.0020515 | 2 | 15 | 11.1 | 0.013041 | 0.015092 | AHU-2 | 0.2 | 15.8761 | 78.8101 | 1x300 |  | AHU-2 | 0.015092 | 0.013041 | 0.015092
SMSB-C&D | UPS-C1 | 0.00016 | 8.39e-05 | 0.0018066 | 2 | 20 | 11.1 | 0.013041 | 0.014847 | UPS-C1 | 0.2 | 16.138 | 80.11 | 2x150 |  | UPS-C1 | 0.014847 | 0.013041 | 0.014847
SMSB-C&D | UPS-D1 | 0.00016 | 8.39e-05 | 0.0018066 | 2 | 20 | 11.1 | 0.013041 | 0.014847 | UPS-D1 | 0.2 | 16.138 | 80.11 | 2x150 |  | UPS-D1 | 0.014847 | 0.013041 | 0.014847
SMSB-C&D | UPS-ACOP | 0.00016 | 8.39e-05 | 0.0018066 | 2 | 20 | 11.1 | 0.013041 | 0.014847 | UPS-ACOP | 0.2 | 16.138 | 80.11 | 2x150 |  | UPS-ACOP | 0.014847 | 0.013041 | 0.014847
SMSB-A&B | LC | 0.00021 | 7.18e-05 | 0.016645 | 2 | 150 | 11.1 | 0.013041 | 0.029686 | LC | 0.2 | 8.0714 | 40.067 | 2x150 |  | LC | 0.029686 | 0.013041 | 0.029686
SMSB-C&D | LC | 0.00021 | 7.18e-05 | 0.016645 | 2 | 150 | 11.1 | 0.013041 | 0.029686 | LC | 0.2 | 8.0714 | 40.067 | 2x150 |  | LC | 0.029686 | 0.013041 | 0.029686
MLP | MLP-B | 0.000409 | 7.24e-05 | 0.024922 | 1 | 60 | 11.1 | 0.014705 | 0.039627 | MLP-B | 0.2 | 6.0466 | 30.0157 | 1x95 |  | MLP-B | 0.039627 | 0.014705 | 0.039627
MLP | MLP-C | 0.000409 | 7.24e-05 | 0.019937 | 1 | 48 | 11.1 | 0.014705 | 0.034643 | MLP-C | 0.2 | 6.9166 | 34.3343 | 1x95 |  | MLP-C | 0.034643 | 0.014705 | 0.034643
MLP | MLP-D | 0.000409 | 7.24e-05 | 0.024922 | 1 | 60 | 11.1 | 0.014705 | 0.039627 | MLP-D | 0.2 | 6.0466 | 30.0157 | 1x95 |  | MLP-D | 0.039627 | 0.014705 | 0.039627
MLP-B | LDB-01B | 0.00394 | 8.37e-05 | 0.078818 | 1 | 20 | 11.1 | 0.039627 | 0.11844 | LDB-01B | 0.2 | 2.0229 | 10.0421 | 10 |  | LDB-01B | 0.11844 | 0.039627 | 0.11844
MLP-C | LDB-01C | 0.00394 | 8.37e-05 | 0.078818 | 1 | 20 | 11.1 | 0.034643 | 0.11346 | LDB-01C | 0.2 | 2.1118 | 10.4832 | 10 |  | LDB-01C | 0.11346 | 0.034643 | 0.11346
MLP-D | LDB-01D | 0.00394 | 8.37e-05 | 0.078818 | 1 | 20 | 11.1 | 0.039627 | 0.11844 | LDB-01D | 0.2 | 2.0229 | 10.0421 | 10 |  | LDB-01D | 0.11844 | 0.039627 | 0.11844
LDB-01B | R1 | 0.00798 |  | 0.399 | 1 | 50 | 11.1 | 0.11844 | 0.51744 | R1 | 0.2 | 0.46306 | 2.2987 | 2.5 |  | R1 | 0.51744 | 0.11844 | 0.51744
LDB-01C | R1 | 0.00798 |  | 0.399 | 1 | 50 | 11.1 | 0.11346 | 0.51246 | R1 | 0.2 | 0.46756 | 2.321 | 2.5 |  | R1 | 0.51246 | 0.11346 | 0.51246
LDB-01D | R1 | 0.00798 |  | 0.399 | 1 | 50 | 11.1 | 0.11844 | 0.51744 | R1 | 0.2 | 0.46306 | 2.2987 | 2.5 |  | R1 | 0.51744 | 0.11844 | 0.51744
AHU-1 | AHU PANEL-B | 0.000409 | 7.24e-05 | 0.024922 | 1 | 60 | 11.1 | 0.015092 | 0.040014 | AHU PANEL-B | 0.2 | 5.9881 | 29.7254 | 1x95 |  | AHU PANEL-B | 0.040014 | 0.015092 | 0.040014
AHU-2 | AHU PANEL-C | 0.000409 | 7.24e-05 | 0.019937 | 1 | 48 | 11.1 | 0.015092 | 0.03503 | AHU PANEL-C | 0.2 | 6.8402 | 33.955 | 1x95 |  | AHU PANEL-C | 0.03503 | 0.015092 | 0.03503
AHU-2 | AHU PANEL-D | 0.000409 | 7.24e-05 | 0.024922 | 1 | 60 | 11.1 | 0.015092 | 0.040014 | AHU PANEL-D | 0.2 | 5.9881 | 29.7254 | 1x95 |  | AHU PANEL-D | 0.040014 | 0.015092 | 0.040014
AHU PANEL-C | AHU-41C | 0.00394 | 8.84e-05 | 0.11823 | 1 | 30 | 11.1 | 0.03503 | 0.15326 | AHU-41C | 0.2 | 1.5634 | 7.7609 | 1x6 |  | AHU-41C | 0.15326 | 0.03503 | 0.15326
MLP-C | LDB-41C | 0.00394 | 8.37e-05 | 0.11823 | 1 | 30 | 11.1 | 0.034643 | 0.15287 | LDB-41C | 0.2 | 1.5674 | 7.7807 | 1x10 |  | LDB-41C | 0.15287 | 0.034643 | 0.15287
UPS-B1 | UPSBBT-B | 0.000129 | 8.36e-05 | 0.0053802 | 2 | 70 | 11.1 | 0.015751 | 0.021131 | UPSBBT-B | 0.2 | 11.3392 | 56.2884 | 2x185 |  | UPSBBT-B | 0.021131 | 0.015751 | 0.021131
UPS-C1 | UPSBBT-C | 0.000129 | 8.36e-05 | 0.0053802 | 2 | 70 | 11.1 | 0.014847 | 0.020228 | UPSBBT-C | 0.2 | 11.8455 | 58.8021 | 2x185 |  | UPSBBT-C | 0.020228 | 0.014847 | 0.020228
UPS-D1 | UPSBBT-D | 0.000129 | 8.36e-05 | 0.0053802 | 2 | 70 | 11.1 | 0.014847 | 0.020228 | UPSBBT-D | 0.2 | 11.8455 | 58.8021 | 2x185 |  | UPSBBT-D | 0.020228 | 0.014847 | 0.020228
UPSBBT-B | UPS FDB-01B | 0.000931 | 0.000103 | 0.01405 | 1 | 15 | 11.1 | 0.021131 | 0.035181 | UPS FDB-01B | 0.2 | 6.8107 | 33.8087 | 1x25 |  | UPS FDB-01B | 0.035181 | 0.021131 | 0.035181
UPSBBT-C | UPS FDB-01C | 0.000931 | 0.000103 | 0.01405 | 1 | 15 | 11.1 | 0.020228 | 0.034278 | UPS FDB-01C | 0.2 | 6.9902 | 34.6996 | 1x25 |  | UPS FDB-01C | 0.034278 | 0.020228 | 0.034278
UPSBBT-D | UPS FDB-01C | 0.000931 | 0.000103 | 0.01405 | 1 | 15 | 11.1 | 0.020228 | 0.034278 | UPS FDB-01C | 0.2 | 6.9902 | 34.6996 | 1x25 |  | UPS FDB-01C | 0.034278 | 0.020228 | 0.034278
UPS FDB-01B | UDB-01B | 0.00147 | 8.08e-05 | 0.022083 | 1 | 15 | 11.1 | 0.035181 | 0.057264 | UDB-01B | 0.2 | 4.1842 | 20.7708 | 1x16 |  | UDB-01B | 0.057264 | 0.035181 | 0.057264
UPS FDB-01C | UDB-01C | 0.00147 | 8.08e-05 | 0.022083 | 1 | 15 | 11.1 | 0.034278 | 0.056361 | UDB-01C | 0.2 | 4.2513 | 21.1037 | 1x16 |  | UDB-01C | 0.056361 | 0.034278 | 0.056361
UPS FDB-01C | UDB-01D | 0.00147 | 8.08e-05 | 0.022083 | 1 | 15 | 11.1 | 0.034278 | 0.056361 | UDB-01D | 0.2 | 4.2513 | 21.1037 | 1x16 |  | UDB-01D | 0.056361 | 0.034278 | 0.056361
UDB-01B | R1 | 0.00798 |  | 0.399 | 1 | 50 | 11.1 | 0.057264 | 0.45626 | R1 | 0.2 | 0.52515 | 2.6069 | 2.5 |  | R1 | 0.45626 | 0.057264 | 0.45626
UDB-01C | R1 | 0.00798 |  | 0.399 | 1 | 50 | 11.1 | 0.056361 | 0.45536 | R1 | 0.2 | 0.52619 | 2.6121 | 2.5 |  | R1 | 0.45536 | 0.056361 | 0.45536
UDB-01D | R1 | 0.00798 |  | 0.399 | 1 | 50 | 11.1 | 0.056361 | 0.45536 | R1 | 0.2 | 0.52619 | 2.6121 | 2.5 |  | R1 | 0.45536 | 0.056361 | 0.45536