## Capacitor Size
Size of Capacitor Bank for Power Factor Correction
Size of Capacitor Bank |  |  |  | Annual Saving and Pay Back Period |  |  | Designing & Configuration of Capacitor Bank
Capacitor Details: |  |  |  | Before Power Factor Correction
System Voltage | 3 | Phase | 1.732 | Electrical Load | 81.9805 | Kva |  | Size of Capacitor Bank |  | 60 | Kvar |  |  | #REF! | #REF! | Kw | 2.5 | $
Capacitor Line Voltage | 415 | Volt |  | Load Current | 114.0551 | Amp |  | Capacitor Voltage |  | 415 | Volt |  |  |  |  | Kva | 5 | £
Capacitor Connected in | Star |  |  | KVA Demand Charge | 8198.0529 | Rs |  | No of Steps |  | 6 | 25 |  |  |  |  | Star | 7.5 | €
Capacitor Cost / Kva | 60 | Rs |  | Unit Consumed / Year | 543120 | Kwh |  | Targeted Power Factor |  | 0.98 | 98 |  |  |  |  | Delta | 10 | ¥
Annual Intrest & Depriciation/Capacitor | 12% |  |  | Energy Charge/Year | 5431200 | Rs |  | CT Ratio |  | 200 | 5 |  |  |  |  | 1 | 15 | Rs
|  |  |  | Total Annual Cost | 5439398.0529 | Rs | [9 empty] | 3 | 20
Electricity Terrif Details: |  |  |  | Capital Cost of capacitor | - | Rs |  | Steps & Size of Capacitor in Capacitor Bank | [8 empty] | 25
Daily Working Hours | 24 |  |  | Annual Inte and Dep | - | Rs |  | Step | Actual kvar | Power Ratio | Kvar | Amp |  |  |  |  | 35
Electricity Charge / Kva | 100 | Rs |  | Total Annual Cost | 5439398.0529 | Rs |  | 1 | 25 | 1 | 25 | 34.0855 |  |  |  |  | 50
Electricity Charge / Kw | 10 | Rs | [5 empty] | 2 | 5 | 0.2 | 5 | 6.8171 |  |  |  |  | 60
|  |  |  | After Power Factor Correction |  |  |  | 3 | 10 | 0.4 | 10 | 13.6342 |  |  |  |  | 75
Size of Capacitor Bank |  |  |  | Electrical Load | 69.161 | Kva |  | 4 | 5 | 0.2 | 5 | 6.8171 |  |  |  |  | 100
Leading KVAR | 32.3304 | Kvar |  | Load Current | 96.22 | Amp |  | 5 | 5 | 0.2 | 5 | 6.8171 |  |  |  |  | 125
Leading KVAR supplied by each Phase | 10.7768 | Kvar / Phase |  | KVA Demand Charge | 6916.0998 | Rs |  | 6 | 10 | 0.4 | 10 | 13.6342 |  |  |  |  | 150
Capacitor Charging Current (Ic) | 44.9249 | Amp |  | Unit Consumed/Year | 543120 | Kwh | [10 empty] | 175
Capacitance of Capacitor | 596.1227 | μF | 75361.9047 | Energy Charge/Year | 5431200 | Rs | [10 empty] | 200
Required No of Capacitor | 3 No of | 10.78 Kvar |  | Total Annual Cost | 5438116.0998 | Rs | [10 empty] | 225
Required Size of Capacitor Bank | 32 | Kvar |  | Capital Cost of capacitor | 4918.8317 | Rs | [10 empty] | 250
|  |  |  | Annual Interest and Deprecation | 590.2598 | Rs | [10 empty] | 300
Protection of Capacitor Bank |  |  |  | Total Annual Cost | 5438706.3596 | Rs | [10 empty] | 400
Size of Main Fuse of Capacitor Bank | 89.8499 | Amp | [5 empty] | Total: | 60 | 2.4 | 60 | 81.8053 | 1
Size of Circuit Breaker (Nr. This Value) | 67.3874 | Amp |  | Pay Back Period
Thermal Setting of Circuit Breaker | 67.3874 | Amp |  | Annual Cost before P.F Correction: | 5439398.0529 | Rs |  | Actual Size of Capacitor Bank |  |  | 60 | Kvar
Magnetic Setting of Circuit Breaker | 449.2494 | Amp |  | Annual Cost After P.F Correction: | 5438706.3596 | Rs |  | Minimum Main Circuit Breaker Rating |  |  | 122.7079 | Amp
Size of Cable For Capacitor Connection | 64.2427 | Amp |  | Annual Saving | 691.6933 | Rs |  | Step Combination |  |  | 1,0.2,0.4,0.2,0.2,0.4,,,,,,
Discharge Resistior for Capacitor |  |  |  | Pay Back Period | 7.1113 | Years |  | C/K Value |  |  | 0.17391
[8 empty] | Design of Capacitor Bank |  | O.K

## Electrical Load
Total Connected Load
Sr.No | Equipment | Load (Kw) | No | Total (Kw) | Efficiency | Old P.F | Target P.F | Kva (old) | Kva (New) | Kvar
1 |  | 18.5 | 2 | 37 | 90% | 0.82 | 0.98 | 50.1355 | 41.9501 | 20.3478 | 0.698 | 0.20306 | 41.1111
2 |  | 7.5 | 2 | 15 | 90% | 0.83 | 0.98 | 20.0803 | 17.0068 | 7.8158 | 0.672 | 0.20306 | 16.6667
3 |  | 10 | 1 | 10 | 100% | 0.85 | 0.98 | 11.7647 | 10.2041 | 4.1669 | 0.61974 | 0.20306 | 10
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  |  | 62 |  |  |  | 81.9805 | 69.161 | 32.3304 |  |  | 67.7778