## 2
VOLTAGE DROP CALCULATION
Serial No. | CABLE ROUTE |  | CABLE LENGTH (M) | INSTALLATION |  | CONNECTED LOAD (KVA) | CURRENT DESIGNED (lb AMP) | CIRCUIT BREAKER RATING (AMP) (150 % of lb) | CIRCUIT BREAKER PROPOSED (AMP) Ic | DERATING FACTORS |  |  |  |  | CURRRENT CARRYING CAPACITY REQUIRED Ia = Ic T1 x T2 | CABLE CURRENT RATING (AMP) | CABLE SIZE | VOLTAGE DROP |  | VOLTAGE REGULATION | CABLE SIZE AS PER CONTRACT | REMARKS
[10 empty] | DIRECT BURRIED |  |  | IN AIR
| From | To |  | LOCATION (T2) | TYPE (T1) |  |  |  |  | Variation of depth (T1) | Variation of Temp. (T2) | Variation of Resistivity (T3) | Grouping Factor (T1) | Variation of Temp. (T2) |  |  |  | vd mv/A/m | VOLTAGE DROP (vd) | % = vd x 100 Vs
1 | SWGR-1 | MDP1 | 150 | NO CEILING | CABLE TRAY | 50 | 75.9671 | 113.9507 | 125 |  |  |  | 0.85 | 0.96 | 153.1863 | 345 | 4C-120mm2 Cu XLPE PVC CABLE | 0.368 | 4.1934 | 1.1035 | 3(3.5-300mm2) |  | 5 | 3 | 30 | 15
| MDP1 | SMDP1 | 0 | OUTDOOR | PVC DUCT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.82 | 48.7805 | 784 | 2(3.5C-150mm2 Cu XLPE PVC CABLE) | 0.1575 | 0 | 0 | 2(3.5-150mm2) |  | 1 | 4 | 38 | 9
| SMDP1 | PG1 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 32 |  |  |  | 0.85 | 0.91 | 41.3704 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 | 4C-25mm |  | 5 | 2 | 15 | 8
| PG1 | LOAD | 0 | ABOVE CEILING | CONDUIT | 0 | 0 | 0 | 32 |  |  |  | 1 | 0.91 | 35.1648 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  | 1.1035 | 4 | 2 | 3 | 8
2 | SMDP1 | PG6 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 100 |  |  |  | 0.85 | 0.91 | 129.2825 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 | 4C-25mm2 |  | 5 | 2 | 15 | 13
| PG6 | LOAD | 0 | ABOVE CEILING | CONDUIT | 0 | 0 | 0 | 25 |  |  |  | 1 | 0.91 | 27.4725 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 2 | 3 | 7
3 | SMDP1 | PG7 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 32 |  |  |  | 0.85 | 0.91 | 41.3704 | 46 | 4C-4.0mm2 Cu XLPE PVC CABLE | 8.747 | 0 | 0 | 4C-4.0mm2 |  | 5 | 2 | 11 | 8
| PG7 | LOAD | 0 | ABOVE CEILING | CONDUIT | 0 | 0 | 0 | 25 |  |  |  | 1 | 0.91 | 27.4725 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 2 | 3 | 7
| SMDP1 | PG8 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 25 |  |  |  | 0.85 | 0.91 | 32.3206 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 | 4C-25mm2 |  | 5 | 2 | 15 | 7
| PG8 | LOAD | 0 | ABOVE CEILING | CONDUIT | 0 | 0 | 0 | 25 |  |  |  | 1 | 0.91 | 27.4725 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 2 | 3 | 7
| SMDP1 | PG9 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 25 |  |  |  | 0.85 | 0.91 | 32.3206 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 | 4C-10mm2 |  | 5 | 2 | 13 | 7
| PG9 | LOAD | 0 | ABOVE CEILING | CONDUIT | 0 | 0 | 0 | 25 |  |  |  | 1 | 0.91 | 27.4725 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 2 | 3 | 7
| SMDP1 | PG10 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 25 |  |  |  | 0.85 | 0.91 | 32.3206 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 | 4C-25mm2 |  | 5 | 2 | 15 | 7
| PG10 | LOAD | 0 | ABOVE CEILING | CONDUIT | 0 | 0 | 0 | 25 |  |  |  | 1 | 0.91 | 27.4725 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 2 | 3 | 7
| SMDP1 | PG11 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.91 | 51.713 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 | 4C-25mm2 |  | 5 | 2 | 15 | 9
| PG11 | LOAD | 0 | ABOVE CEILING | CONDUIT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.91 | 43.956 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 2 | 3 | 9
| SMDP1 | X-RAY | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.91 | 51.713 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 | 4C-25mm2 |  | 5 | 2 | 15 | 9
| MDP1 | SMDP2 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.91 | 51.713 | 240 | 4C-70mm2 Cu XLPE PVC CABLE | 0.585 | 0 | 0 | 4C-70mm2 |  | 5 | 2 | 28 | 9
| SMDP2 | PF2 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.91 | 51.713 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 | 4C-10mm2 |  | 5 | 2 | 13 | 9
| PF2 | LOAD | 0 | ABOVE CEILING | CONDUIT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.91 | 43.956 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 2 | 3 | 9
| SMDP2 | PF3 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.91 | 51.713 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 | 4C-10mm2 |  | 5 | 2 | 13 | 9
| PF3 | LOAD | 0 | ABOVE CEILING | CONDUIT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.91 | 43.956 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 2 | 3 | 9
| SMDP2 | PR | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.91 | 51.713 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 | 4C-10mm2 |  | 5 | 2 | 13 | 9
| PR | LOAD | 0 | OUTDOOR | CONDUIT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.82 | 48.7805 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 4 | 3 | 9
| MDP1 | GHOUSE | 0 | OUTDOOR | PVC DUCT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.82 | 48.7805 | 56 | 4C-6.0mm2 Cu XLPE PVC CABLE | 5.871 | 0 | 0 | 4C-6mm2 |  | 1 | 4 | 12 | 9
| GHOUSE | LOAD | 0 | NO CEILING | CONDUIT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.96 | 41.6667 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 3 | 3 | 9
| MDP1 | KIDNEY | 0 | OUTDOOR | PVC DUCT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.82 | 48.7805 | 690 | 2(4C-120mm2 Cu XLPE PVC CABLE) | 0.184 | 0 | 0 | 2(4C-120mm2) |  | 1 | 4 | 58 | 9
| MDP1 | NSTAFF | 0 | OUTDOOR | PVC DUCT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.82 | 48.7805 | 538 | 4C-240mm2 Cu XLPE PVC CABLE | 0.226 | 0 | 0 | 4C-240mm2 |  | 1 | 4 | 33 | 9
| MDP1 | PA-ANC | 0 | NO CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.96 | 49.0196 | 99 | 4C-16mm2 Cu XLPE PVC CABLE | 2.239 | 0 | 0 | 4C-16mm2 |  | 5 | 3 | 14 | 9
| SW1 | MDPAC1 | 0 | NO CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.96 | 49.0196 | 1878 | 3(3.5C-300mm2 Cu XLPE PVC CABLE) | 0.066 | 0 | 0 | 3(3.5C-300mm2) |  | 5 | 3 | 48 | 9
| MDPAC1 | SMDPAC1 | 0 | OUTDOOR | PVC DUCT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.82 | 48.7805 | 440 | 3.5C-185mm2 Cu XLPE PVC CABLE | 0.27 | 0 | 0 | 3.5C-185mm2 |  | 1 | 4 | 22 | 9
| SMDPAC1 | PGAC1 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.91 | 51.713 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 | 4C-25mm2 |  | 5 | 2 | 15 | 9
| PGAC1 | LOAD | 0 | ABOVE CEILING | CONDUIT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.91 | 43.956 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 2 | 3 | 9
| SMDPAC1 | KITCHEN | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.91 | 51.713 | 298 | 3.5C-95mm2 Cu XLPE PVC CABLE | 0.444 | 0 | 0 | 3.5C-95mm2 |  | 5 | 2 | 19 | 9
| SMDPAC1 | STRELI | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.91 | 51.713 | 240 | 4C-70mm2 Cu XLPE PVC CABLE | 0.585 | 0 | 0 | 4C-70mm2 |  | 5 | 2 | 28 | 9
| SMDPAC1 | PGAC2 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.91 | 51.713 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 | 4C-25mm2 |  | 5 | 2 | 15 | 9
| PGAC2 | LOAD | 0 | ABOVE CEILING | CONDUIT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.91 | 43.956 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 2 | 3 | 9
| MDPAC1 | SMDPAC2 | 0 | OUTDOOR | PVC DUCT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.82 | 48.7805 | 199 | 4C-50mm2 Cu XLPE PVC CABLE | 0.809 | 0 | 0 | 4C-50mm2 |  | 1 | 4 | 27 | 9
| SMDPAC2 | PFAC1 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.91 | 51.713 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 | 4C-25mm2 |  | 5 | 2 | 15 | 9
| PFAC1 | LOAD | 0 | ABOVE CEILING | CONDUIT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.91 | 43.956 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 2 | 3 | 9
| MDPAC1 | SMDPAC3 | 0 | OUTDOOR | PVC DUCT | 0 | 0 | 0 | 40 |  |  |  | 1 | 0.82 | 48.7805 | 1252 | 2(3.5C-300mm2 Cu XLPE PVC CABLE) | 0.099 | 0 | 0 | 2(3.5C-300mm2) |  | 1 | 4 | 41 | 9
| SMDPAC3 | PU-1 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.91 | 51.713 | 298 | 4C-95mm2 Cu XLPE PVC CABLE | 0.444 | 0 | 0 | 4C-95mm2 |  | 5 | 2 | 29 | 9
| SMDPAC3 | PU-2 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 40 |  |  |  | 0.85 | 0.91 | 51.713 | 99 | 4C-16mm2 Cu XLPE PVC CABLE | 2.239 | 0 | 0 | 4C-16mm2 |  | 5 | 2 | 14 | 9
| SMDPAC3 | PU-4 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 25 |  |  |  | 0.85 | 0.91 | 32.3206 | 161 | 4C-35mm2 Cu XLPE PVC CABLE | 1.063 | 0 | 0 | 4C-35mm2 |  | 5 | 2 | 16 | 7
| SMDPAC3 | PU-5 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 25 |  |  |  | 0.85 | 0.91 | 32.3206 | 161 | 4C-35mm2 Cu XLPE PVC CABLE | 1.063 | 0 | 0 | 4C-35mm2 |  | 5 | 2 | 16 | 7
| SMDPAC3 | PU-6 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 25 |  |  |  | 0.85 | 0.91 | 32.3206 | 298 | 4C-95mm2 Cu XLPE PVC CABLE | 0.444 | 0 | 0 | 4C-95mm2 |  | 5 | 2 | 29 | 7
| SMDPAC3 | PU-9 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 25 |  |  |  | 0.85 | 0.91 | 32.3206 | 298 | 4C-95mm2 Cu XLPE PVC CABLE | 0.444 | 0 | 0 | 4C-95mm2 |  | 5 | 2 | 29 | 7
| SMDPAC3 | PU-11 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 25 |  |  |  | 0.85 | 0.91 | 32.3206 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 | 4C-25mm2 |  | 5 | 2 | 15 | 7
| SMDPAC3 | PU-12 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 25 |  |  |  | 0.85 | 0.91 | 32.3206 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 | 4C-25mm2 |  | 5 | 2 | 15 | 7
| SMDPAC3 | PU-13 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 25 |  |  |  | 0.85 | 0.91 | 32.3206 | 298 | 4C-95mm2 Cu XLPE PVC CABLE | 0.444 | 0 | 0 | 4C-95mm2 |  | 5 | 2 | 29 | 7
| SMDPAC3 | PRAC1 | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 25 |  |  |  | 0.85 | 0.91 | 32.3206 | 56 | 4C-6.0mm2 Cu XLPE PVC CABLE | 5.871 | 0 | 0 | 4C-6mm2 |  | 5 | 2 | 12 | 7
| PRAC1 | LOAD | 0 | ABOVE CEILING | CONDUIT | 0 | 0 | 0 | 25 |  |  |  | 1 | 0.91 | 27.4725 | 49 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 0 | 0 |  |  | 4 | 2 | 3 | 7
| SMDPAC3 | PEF | 0 | ABOVE CEILING | CABLE TRAY | 0 | 0 | 0 | 25 |  |  |  | 0.85 | 0.91 | 32.3206 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 | 4C-10mm2 |  | 5 | 2 | 13 | 7
| MDPAC1 | LAUNDRY | 0 | NO CEILING | CABLE TRAY | 0 | 0 | 0 | 25 |  |  |  | 0.85 | 0.96 | 30.6373 | 161 | 4C-35mm2 Cu XLPE PVC CABLE | 1.063 | 0 | 0 | 4C-35mm2 |  | 5 | 3 | 16 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT | 0 | 0 | 0 | 25 |  |  |  | 1 | 0.91 | 27.4725 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 |  |  | 1 | 2 | 13 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 0 | 0 | 0 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 |  |  | 2 | 2 | 13 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 |  |  | 2 | 2 | 13 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 |  |  | 2 | 2 | 13 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 |  |  | 2 | 2 | 13 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 |  |  | 2 | 2 | 13 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 |  |  | 2 | 2 | 15 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 |  |  | 2 | 2 | 13 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 99 | 4C-16mm2 Cu XLPE PVC CABLE | 2.239 | 0 | 0 |  |  | 2 | 2 | 14 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 |  |  | 2 | 2 | 13 | 7
|  |  | 0 | OUTDOOR | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.82 | 37.6393 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 |  |  | 2 | 4 | 15 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 |  |  | 2 | 2 | 13 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 |  |  | 2 | 2 | 13 | 7
|  |  | 0 | ABOVE CEILING | CABLE TRAY | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.85 | 0.91 | 32.3206 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 |  |  | 5 | 2 | 13 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 |  |  | 2 | 2 | 13 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 76 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 0 | 0 |  |  | 2 | 2 | 13 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 25 |  |  |  | 0.81 | 0.91 | 33.9167 | 135 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 0 | 0 |  |  | 2 | 2 | 15 | 7
|  |  | 0 | ABOVE CEILING | PVC DUCT(2Ckt.) | 8.59 | 13.0512 | 19.5767 | 32 |  |  |  | 0.81 | 0.91 | 43.4134 | 440 | 3.5C-185mm2 Cu XLPE PVC CABLE | 0.27 | 0 | 0 |  |  | 2 | 2 | 22 | 8
3
11

## 1
STANDARD CIRCUIT BREAKER RATING
| BREAKER (AT) | BREAKER (AF) | TYPE | BREAKER (AF) | TYPE | BREAKER (AF) | TYPE | BREAKER (AF) | TYPE | BREAKER (AF) | TYPE | BREAKER (AF) | TYPE | BREAKER (AF) | TYPE | BREAKER (AF) | TYPE | WIRE & CABLE |  | GROUND |  | REMARKS
[18 empty] | mm2 | AWG | mm2 | AWG
| 0.5 | 63 | MCB
| 0.75 | 63 | MCB
| 1 | 63 | MCB
| 2 | 63 | MCB
| 2.5 |  |  | 100 | MCCB | 160 | MCCB | 250 | MCCB
| 3 | 63 | MCB
| 4 | 63 | MCB
| 6 | 63 | MCB
| 6.3 |  |  | 100 | MCCB | 160 | MCCB | 250 | MCCB
1 | 10 | 63 | MCB | 100 | MCCB | 160 | MCCB | 250 | MCCB
2 | 12.5 |  |  | 100 | MCCB | 160 | MCCB | 250 | MCCB
3 | 13 | 63 | MCB
4 | 15 | 63 | MCB | [14 empty] | 2.5 | 14 | 2.5 | 14 | BRANCH CIRCUIT
5 | 16 | 63 | MCB | 100 | MCCB | 160 | MCCB | 250 | MCCB | [8 empty] | 2.5 | 14 | 2.5 | 14 | BRANCH CIRCUIT
6 | 20 | 63 | MCB | 100 | MCCB | 160 | MCCB | 250 | MCCB | [8 empty] | 4 | 12 | 4 | 12 | BRANCH CIRCUIT
7 | 25 | 63 | MCB | 100 | MCCB | 160 | MCCB | 250 | MCCB | [8 empty] | 4 | 12 | 4 | 12 | BRANCH CIRCUIT
8 | 32 | 63 | MCB | 100 | MCCB | 160 | MCCB | 250 | MCCB | [8 empty] | 6 | 10 | 6 | 10 | BRANCH CIRCUIT
9 | 40 | 63 | MCB | 100 | MCCB | 160 | MCCB | 250 | MCCB | [8 empty] | 10 | 8 | 6 | 10 | BRANCH CIRCUIT
10 | 50 | 63 | MCB | 100 | MCCB | 160 | MCCB | 250 | MCCB | [8 empty] | 16 | 6 | 6 | 10 | BRANCH CIRCUIT
11 | 63 | 63 | MCB | 100 | MCCB | 160 | MCCB | 250 | MCCB | [10 empty] | 6 | 10
12 | 80 |  |  | 100 | MCCB | 160 | MCCB | 250 | MCCB | [10 empty] | 6 | 10 |  | 80 / 100
13 | 100 |  |  | 100 | MCCB | 160 | MCCB | 250 | MCCB | [10 empty] | 6 | 10 |  | 100 / 100
14 | 120 | [8 empty] | 400 | MCCB | [8 empty] | 10 | 8 |  | 120 / 120
15 | 125 |  |  |  |  | 160 | MCCB | 250 | MCCB | [10 empty] | 10 | 8 |  | 125 / 160
16 | 150 |  |  |  |  | 160 | MCCB | 250 | MCCB | 400 | MCCB | [8 empty] | 10 | 8 |  | 150 / 160
17 | 160 |  |  |  |  | 160 | MCCB | 250 | MCCB | [10 empty] | 10 | 8 |  | 160 / 160
18 | 200 | [6 empty] | 250 | MCCB | 400 | MCCB | [8 empty] | 16 | 6 |  | 200 / 250
19 | 220 | [6 empty] | 250 | MCCB | [10 empty] | 16 | 6 |  | 220 / 250
20 | 250 | [6 empty] | 250 | MCCB | 400 | MCCB | [8 empty] | 16 | 6 |  | 250 / 250
21 | 300 | [18 empty] | 25 | 4 |  | 300 / 300
22 | 320 | [8 empty] | 400 | MCCB | [8 empty] | 35 | 3 |  | 320 / 400
23 | 400 | [8 empty] | 400 | MCCB | [8 empty] | 50 | 1 |  | 400 / 400
24 | 500 | [10 empty] | 630 | MCCB | [6 empty] | 70 | 1 |  | 500 / 630
25 | 630 | [10 empty] | 630 | MCCB | 630 | MCCB | 630 | ACB |  |  | 95 | 3 |  | 630 / 630
26 | 800 | [12 empty] | 800 | MCCB | 800 | ACB |  |  | 95 | 3 |  | 800 / 800
27 | 1000 | [12 empty] | 1000 | MCCB | 1000 | ACB |  |  | 95 | 3 |  | 1000 / 1000
28 | 1200 | [14 empty] | 1200 | ACB |  |  | 95 | 3 |  | 1200 / 1200
29 | 1250 | [12 empty] | 1250 | MCCB | 1250 | ACB |  |  | 95 | 3 |  | 1250 / 1250
30 | 1600 | [12 empty] | 1600 | MCCB | 1600 | ACB |  |  | 120 | 4 |  | 1600 / 1600
31 | 2000 | [14 empty] | 2000 | ACB |  |  | 150 | 250 |  | 2000 / 2000
32 | 2500 | [14 empty] | 2500 | ACB |  |  | 185 | 350 |  | 2500 / 2500
33 | 3200 | [14 empty] | 3200 | ACB |  |  | 240 | 400 |  | 3200 / 3200
34 | 4000 | [14 empty] | 4000 | ACB |  |  | 300 | 500 |  | 4000 / 4000
35 | 5000 | [14 empty] | 5000 | ACB |  |  | 400 | 700 |  | 5000 / 5000
36 | 6300 | [14 empty] | 6300 | ACB |  |  | 500 | 800 |  | 6300 / 6300

## 3
CABLE SIZING CALCULATION
Serial No. | DESCRIPTION | VOLTAGE DROP (Mv/Amp/meter) | AMPACITY
|  |  | IN GROUND | IN DUCT | IN AIR
1 | 2C-1.5mm2 Cu PVC/PVC CABLE | 22.476 | 33 | 27 | 27
2 | 2C-2.5mm2 Cu PVC/PVC CABLE | 13.8 | 41 | 35 | 35
3 | 2C-4.0mm2 Cu PVC/PVC CABLE | 8.624 | 55 | 45 | 49
4 | 2C-6.0mm2 Cu PVC/PVC CABLE | 5.791 | 68 | 56 | 63
5 | 2C-10mm2 Cu PVC/PVC CABLE | 3.474 | 89 | 77 | 84
6 | 2C-16mm2 Cu PVC/PVC CABLE | 2.212 | 116 | 91 | 112
7 | 2C-25mm2 Cu PVC/PVC CABLE | 1.43 | 150 | 119 | 147
8 | 2C-35mm2 Cu PVC/PVC CABLE | 1.053 | 177 | 147 | 182
9 | 4C-1.5mm2 Cu XLPE PVC CABLE | 22.82 | 30 | 27 | 25
10 | 4C-2.5mm2 Cu XLPE PVC CABLE | 14.01 | 40 | 34 | 36
11 | 4C-4.0mm2 Cu XLPE PVC CABLE | 8.747 | 51 | 42 | 46
12 | 4C-6.0mm2 Cu XLPE PVC CABLE | 5.871 | 65 | 53 | 56
13 | 4C-10mm2 Cu XLPE PVC CABLE | 3.519 | 86 | 70 | 76
14 | 4C-16mm2 Cu XLPE PVC CABLE | 2.239 | 111 | 88 | 99
15 | 4C-25mm2 Cu XLPE PVC CABLE | 1.114 | 146 | 119 | 135
16 | 4C-35mm2 Cu XLPE PVC CABLE | 1.063 | 177 | 140 | 161
17 | 3.5C-50mm2 Cu XLPE PVC CABLE | 0.809 | 211 | 170 | 199
18 | 3.5C-70mm2 Cu XLPE PVC CABLE | 0.585 | 251 | 211 | 240
19 | 3.5C-95mm2 Cu XLPE PVC CABLE | 0.444 | 302 | 246 | 298
20 | 3.5C-120mm2 Cu XLPE PVC CABLE | 0.368 | 348 | 287 | 345
21 | 3.5C-150mm2 Cu XLPE PVC CABLE | 0.315 | 382 | 322 | 392
22 | 3.5C-185mm2 Cu XLPE PVC CABLE | 0.27 | 428 | 363 | 440
23 | 3.5C-240mm2 Cu XLPE PVC CABLE | 0.226 | 496 | 427 | 538
24 | 3.5C-300mm2 Cu XLPE PVC CABLE | 0.198 | 559 | 474 | 626
25 | 3.5C-400mm2 Cu XLPE PVC CABLE | 0.176 | 638 | 544 | 720
26 | 3.5C-500mm2 Cu XLPE PVC CABLE | 0.158 | 718 | 620 | 819
27 | 4C-50mm2 Cu XLPE PVC CABLE | 0.809 | 211 | 170 | 199
28 | 4C-70mm2 Cu XLPE PVC CABLE | 0.585 | 251 | 211 | 240
29 | 4C-95mm2 Cu XLPE PVC CABLE | 0.444 | 302 | 246 | 298
30 | 4C-120mm2 Cu XLPE PVC CABLE | 0.368 | 348 | 287 | 345
31 | 4C-150mm2 Cu XLPE PVC CABLE | 0.315 | 382 | 322 | 392
32 | 4C-185mm2 Cu XLPE PVC CABLE | 0.27 | 428 | 363 | 440
33 | 4C-240mm2 Cu XLPE PVC CABLE | 0.226 | 496 | 427 | 538
34 | 4C-300mm2 Cu XLPE PVC CABLE | 0.198 | 559 | 474 | 626
35 | 4C-400mm2 Cu XLPE PVC CABLE | 0.176 | 638 | 544 | 720
36 | 4C-500mm2 Cu XLPE PVC CABLE | 0.158 | 718 | 620 | 819
37 | 2(3.5C-120mm2 Cu XLPE PVC CABLE) | 0.184 | 696 | 574 | 690
38 | 2(3.5C-150mm2 Cu XLPE PVC CABLE) | 0.1575 | 764 | 644 | 784
39 | 2(3.5C-185mm2 Cu XLPE PVC CABLE) | 0.135 | 856 | 726 | 880
40 | 2(3.5C-240mm2 Cu XLPE PVC CABLE) | 0.113 | 992 | 854 | 1076
41 | 2(3.5C-300mm2 Cu XLPE PVC CABLE) | 0.099 | 1118 | 948 | 1252
42 | 2(3.5C-400mm2 Cu XLPE PVC CABLE) | 0.088 | 1276 | 1088 | 1440
43 | 2(3.5C-500mm2 Cu XLPE PVC CABLE) | 0.079 | 1436 | 1240 | 1638
44 | 3(3.5C-120mm2 Cu XLPE PVC CABLE) | 0.1227 | 1044 | 861 | 1035
45 | 3(3.5C-150mm2 Cu XLPE PVC CABLE) | 0.105 | 1146 | 966 | 1176
46 | 3(3.5C-185mm2 Cu XLPE PVC CABLE) | 0.09 | 1284 | 1089 | 1320
47 | 3(3.5C-240mm2 Cu XLPE PVC CABLE) | 0.075 | 1488 | 1281 | 1614
48 | 3(3.5C-300mm2 Cu XLPE PVC CABLE) | 0.066 | 1677 | 1422 | 1878
49 | 3(3.5C-400mm2 Cu XLPE PVC CABLE) | 0.059 | 1914 | 1632 | 2160
50 | 3(3.5C-500mm2 Cu XLPE PVC CABLE) | 0.053 | 2154 | 1860 | 2457
51 | 4(3.5C-120mm2 Cu XLPE PVC CABLE) | 0.092 | 1392 | 1148 | 1380
52 | 4(3.5C-150mm2 Cu XLPE PVC CABLE) | 0.079 | 1520 | 1288 | 1568
53 | 4(3.5C-185mm2 Cu XLPE PVC CABLE) | 0.0675 | 1712 | 1452 | 1760
54 | 4(3.5C-240mm2 Cu XLPE PVC CABLE) | 0.0565 | 1984 | 1708 | 2152
55 | 4(3.5C-300mm2 Cu XLPE PVC CABLE) | 0.0495 | 2236 | 1896 | 2504
56 | 4(3.5C-400mm2 Cu XLPE PVC CABLE) | 0.044 | 2552 | 2176 | 2880
57 | 4(3.5C-500mm2 Cu XLPE PVC CABLE) | 0.0395 | 2872 | 2480 | 3276
58 | 2(4C-120mm2 Cu XLPE PVC CABLE) | 0.184 | 696 | 574 | 690
59 | 2(4C-150mm2 Cu XLPE PVC CABLE) | 0.1575 | 764 | 644 | 784
60 | 2(4C-185mm2 Cu XLPE PVC CABLE) | 0.135 | 856 | 726 | 880
61 | 2(4C-240mm2 Cu XLPE PVC CABLE) | 0.113 | 992 | 854 | 1076
62 | 2(4C-300mm2 Cu XLPE PVC CABLE) | 0.099 | 1118 | 948 | 1252
63 | 2(4C-400mm2 Cu XLPE PVC CABLE) | 0.088 | 1276 | 1088 | 1440
64 | 2(4C-500mm2 Cu XLPE PVC CABLE) | 0.079 | 1436 | 1240 | 1638
65 | 3(4C-120mm2 Cu XLPE PVC CABLE) | 0.1227 | 1044 | 861 | 1035
66 | 3(4C-150mm2 Cu XLPE PVC CABLE) | 0.105 | 1146 | 966 | 1176
67 | 3(4C-185mm2 Cu XLPE PVC CABLE) | 0.09 | 1284 | 1089 | 1320
68 | 3(4C-240mm2 Cu XLPE PVC CABLE) | 0.075 | 1488 | 1281 | 1614
69 | 3(4C-300mm2 Cu XLPE PVC CABLE) | 0.066 | 1677 | 1422 | 1878
70 | 3(4C-400mm2 Cu XLPE PVC CABLE) | 0.059 | 1914 | 1632 | 2160
71 | 3(4C-500mm2 Cu XLPE PVC CABLE) | 0.053 | 2154 | 1860 | 2457
72 | 4(4C-120mm2 Cu XLPE PVC CABLE) | 0.092 | 1392 | 1148 | 1380
73 | 4(4C-150mm2 Cu XLPE PVC CABLE) | 0.079 | 1520 | 1288 | 1568
74 | 4(4C-185mm2 Cu XLPE PVC CABLE) | 0.0675 | 1712 | 1452 | 1760
75 | 4(4C-240mm2 Cu XLPE PVC CABLE) | 0.0565 | 1984 | 1708 | 2152
76 | 4(4C-300mm2 Cu XLPE PVC CABLE) | 0.0495 | 2236 | 1896 | 2504
77 | 4(4C-400mm2 Cu XLPE PVC CABLE) | 0.044 | 2552 | 2176 | 2880
78 | 4(4C-500mm2 Cu XLPE PVC CABLE) | 0.0395 | 2872 | 2480 | 3276
GROUPING FACTOR
1 | PVC DUCT | 1
2 | PVC DUCT(2Ckt.) | 0.81
3 | PVC DUCT(More) | 0.7
4 | CONDUIT | 1
5 | CABLE TRAY | 0.85
TEMPERATURE FACTOR
1 | TUNNEL | 0.87
2 | ABOVE CEILING | 0.91
3 | NO CEILING | 0.96
4 | OUTDOOR | 0.82