## Gutter Nomber
STORM WATER CALCULATIONS
NAME : | Eng. Abdulahameed Emam |  |  |  | As per national standard plumbing code (NSPC)
page No. (325) table (13.6.1) and page no. (326) table (13.6.2).
DATA IN | Different Rainfall rates (inch/Hour) | 1 | 1.5 | 2 | 4 | 5 | 6
| Allowable Projected roof Area (m2) | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Projected Arae (ver) | 1285 | 1749.5 | 1166 | 2043 | 1635 | 1362
| Projected Arae(hor) | 1241 | 1491 | 2136 | 1068 | 1538 | 1282
DATA OUT | Diameter of Vertical Conductor (inches) | 4 | 5 | 5 | 8 | 8 | 8
| Diameter of Horizontal Pipe (inches) | 5 | 6 | 8 | 8 | 10 | 10
| Different Rainfall rates | 1 | 1.5 | 2 | 4 | 5 | 6
| Equivelent Diam. of Cond. | 4 | 5 | 5 | 8 | 8 | 8
| DIAM. OF COND.(in) | SIZING OF VERTICAL CONDUCTOR
ALLOWABLE PROJECTED ROOF AREA
|  | 1in | 1.5 in | 2 in | 4 in | 5 in | 6 in
| 2 | 202 | 151.5 | 101 | 50 | 40 | 33
| 2.5 | 366 | 274.5 | 183 | 91 | 73 | 61
| 3 | 598 | 448.5 | 299 | 149 | 119 | 99
| 4 | 1285 | 963.5 | 642 | 321 | 257 | 214
| 5 | 2333 | 1749.5 | 1166 | 583 | 466 | 388
| 6 | 3790 | 2842.5 | 1895 | 947 | 758 | 631
| 8 | 8175 | 6131 | 4087 | 2043 | 1635 | 1362
| Different Rainfall rates | 1 | 1.5 | 2 | 4 | 5 | 6
| Equivelent Diam. of PIPE | 5 | 6 | 8 | 8 | 10 | 10
| DIAM. OF PIPE(in) | SIZING OF HORIZONTAL CONDUCTOR
ALLOWABLE PROJECTED ROOF AREA AT SLOPE 1/100 (1%)
|  | 1in | 1.5 in | 2 in | 4 in | 5 in | 6 in
| 3 | 305 | 228 | 152 | 76 | 61 | 51
| 4 | 698 | 523 | 349 | 174 | 139 | 116
| 5 | 1241 | 930 | 620 | 310 | 248 | 207
| 6 | 1988 | 1491 | 994 | 497 | 397 | 331
| 8 | 4273 | 3204 | 2136 | 1068 | 854 | 712
| 10 | 7692 | 5769 | 3846 | 1923 | 1538 | 1282
| 12 | 12374 | 9280 | 6187 | 3093 | 2474 | 2062
| 15 | 22110 | 16582 | 11055 | 5527 | 4422 | 3685
| Different Rainfall rates | 1 | 1.5 | 2 | 4 | 5 | 6
| DIAMETER OF GUTTERS REQUIRED (inches) | 8 | 10 | 10 | 10 | 10 | 10
| DIAM. OF GUUTER(inches) | SIZING OF ROOF GUTTERS
MAXIMUM PROJECTED ROOF AREA FOR GUTTERS AT VARIOUS RAINFALLS RATES
|  | 1in | 1.5 in | 2 in | 4 in | 5 in | 6 in
| 3 | 63 | 42 | 31 | 15 | 12 | 10
| 4 | 133 | 89 | 66 | 33 | 26 | 22
| 5 | 232 | 154 | 116 | 58 | 46 | 38
| 6 | 356 | 237 | 178 | 89 | 71 | 59
| 7 | 512 | 341 | 256 | 128 | 102 | 85
| 8 | 739 | 492 | 369 | 184 | 147 | 123
| 10 | 1337 | 891 | 668 | 334 | 267 | 222
NOMBERS OF GUUTERS REQUIRED
|  | 1in | 1.5 in | 2 in | 4 in | 5 in | 6 in
| 3 | 15.873 | 23.8095 | 32.2581 | 66.6667 | 83.3333 | 100
| 4 | 7.5188 | 11.236 | 15.1515 | 30.303 | 38.4615 | 45.4545
| 5 | 4.3103 | 6.4935 | 8.6207 | 17.2414 | 21.7391 | 26.3158
| 6 | 2.809 | 4.2194 | 5.618 | 11.236 | 14.0845 | 16.9492
| 7 | 1.9531 | 2.9326 | 3.9062 | 7.8125 | 9.8039 | 11.7647
| 8 | 1.3532 | 2.0325 | 2.71 | 5.4348 | 6.8027 | 8.1301
| 10 | 0.74794 | 1.1223 | 1.497 | 2.994 | 3.7453 | 4.5045
Note on D5: EDIT YOUR AREA
Note on C6: in meter square (m 2 )

## Storm system
STORM WATER CALCULATIONS
NAME : | Eng. Abdulahameed Emam |  |  |  | As per national standard plumbing code (NSPC)
page No. (325) table (13.6.1) and page no. (326) table (13.6.2).
DATA IN | Different Rainfall rates (inch/Hour) | 1 | 1.5 | 2 | 4 | 5 | 6
| Allowable Projected roof Area (m2) | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Projected Arae (ver) | 1285 | 1749.5 | 1166 | 2043 | 1635 | 1362
| Projected Arae(hor) | 1241 | 1491 | 2136 | 1068 | 1538 | 1282
DATA OUT | Diameter of Vertical Conductor (inches) | 4 | 5 | 5 | 8 | 8 | 8
| Diameter of Horizontal Pipe (inches) | 5 | 6 | 8 | 8 | 10 | 10
| Different Rainfall rates | 1 | 1.5 | 2 | 4 | 5 | 6
| Equivelent Diam. of Cond. | 4 | 5 | 5 | 8 | 8 | 8
| DIAM. OF COND.(in) | SIZING OF VERTICAL CONDUCTOR
ALLOWABLE PROJECTED ROOF AREA
|  | 1in | 1.5 in | 2 in | 4 in | 5 in | 6 in
| 2 | 202 | 151.5 | 101 | 50 | 40 | 33
| 2.5 | 366 | 274.5 | 183 | 91 | 73 | 61
| 3 | 598 | 448.5 | 299 | 149 | 119 | 99
| 4 | 1285 | 963.5 | 642 | 321 | 257 | 214
| 5 | 2333 | 1749.5 | 1166 | 583 | 466 | 388
| 6 | 3790 | 2842.5 | 1895 | 947 | 758 | 631
| 8 | 8175 | 6131 | 4087 | 2043 | 1635 | 1362
| Different Rainfall rates | 1 | 1.5 | 2 | 4 | 5 | 6
| Equivelent Diam. of PIPE | 5 | 6 | 8 | 8 | 10 | 10
| DIAM. OF PIPE(in) | SIZING OF HORIZONTAL CONDUCTOR
ALLOWABLE PROJECTED ROOF AREA AT SLOPE 1/100 (1%)
|  | 1in | 1.5 in | 2 in | 4 in | 5 in | 6 in
| 3 | 305 | 228 | 152 | 76 | 61 | 51
| 4 | 698 | 523 | 349 | 174 | 139 | 116
| 5 | 1241 | 930 | 620 | 310 | 248 | 207
| 6 | 1988 | 1491 | 994 | 497 | 397 | 331
| 8 | 4273 | 3204 | 2136 | 1068 | 854 | 712
| 10 | 7692 | 5769 | 3846 | 1923 | 1538 | 1282
| 12 | 12374 | 9280 | 6187 | 3093 | 2474 | 2062
| 15 | 22110 | 16582 | 11055 | 5527 | 4422 | 3685
Note on D5: EDIT YOUR AREA
Note on C6: in meter square (m 2 )
Note on D8: abdelhamedemam: