## BOQ
BILL OF MATERIAL
PROJECT: |  |  | CAPACITY | 400.4 kWp
Item No | Description of Items | Specification | UOM
1 | PV Solar Module | 325 Wp, Polycrystaline (72 Cells) | Nos | 1232
2 | Solar String Inverter
2.1 | 20kVA, String Inverter | 3 Phase, 400 V AC String Inverter | Nos | 20
2.3 | Data Logger |  | Nos | As per requirement
3 | Array Combiner Box
3.1 | 4-in 4-out | Made up of Poly Carbonate Enclosures have IP - 65, Fuse (only +ve side): 15A, 1000V, Class Type-II DC SPD | Nos | 20
4 | AC CB
4.1 | 100 kW, CRCA metal Sheet make with powder coated, 5-in 1-out with 40A Amp (5Nos) MCCB incoming and 200A (1 Nos) Outgoing, Cu busbar, Type-II, AC SPD, RYB Indocators, IP-65 Outdoor Type Stand mounted. |  | Nos | 4
5 | MAIN ACCB
4.2 | 400kW, CRCA metal Sheet make with powder coated, 4-in 1-out with 200A Amp (4 Nos) MCCB incoming and 800A Outgoing, Cu busbar, Type-II, AC SPD, 1S Class Bidirectional Meter with CT's, RYB Indocators, IP-65 Outdoor Type Stand mounted. |  | Nos | 1
6 | DG Synchronisation Panel
6.1 | 400 kWp with DG Power |  | Nos | 1
7 | Earthing System
7.1 | Earthing Pit and Electrode | According to IS:3043 Standard | Nos | 12
7.2 | Lightning Arrester | ESE Type | Nos | 1
7.3 | 25 X 3 mm | As per IS:3043-1987 | Meter | 1400
8 | Cables
8.1 | Modules to AJB ( Red & Black) | 1C Solar DC Cable | Meter | 1000
8.2 | AJB to Inverter (Red & Black) | 1C Solar DC Cable | Meter | 700
8.3 | Inverter to ACCB | 4C*16 sqmm Cu. Armound, FRLS Cable | Meter | 570
8.4 | ACCB to Main ACCB | 3.5C*240 sqmm Al. Armound, FRLS Cable | Meter | 270
8.5 | Main ACCB To Termination | 3.5C*300 sq .mm Al. Armound FRLS Cable | Meter | 400
8.6 | EARTHING CABLE | Copper Green Cable 6 sq. mm | Meter | 350
9 | Miscellaneous
9.1 | HDPE Pipe |  | Meter | 200
9.2 | HDPE Pipe Elbow and T |  | Nos | As per site requirement
9.3 | Cable Tie |  | Nos | As per site requirement
9.4 | Cable Lugs |  | Nos | As per site requirement
9.5 | MC4 Connectors Male-Female Pair | TUV Approved | Nos | 200
9.6 | Cable Tray | Perforated GI cable tray | RM | As per site requirement
9.7 | Fire Extinguisher | ABC Type (2kg) | Nos | 2
9.8 | Module cleaning Arrangement: Water jet pump, water tank and Borewell with GI pipe and nozzels |  | Nos | 1
9.9 | Inverter Stand with 3mm fibre sheet thickness | GI angle with black paint | Nos | 20
9.10. | Module Mounting Structure | GI with minimum 80 microns coating | Nos | 1 Set
9.11 | Fencing: Brick wall of 1m height from ground level and 0.6 m fencing of 160m length with 1 nos of Gate |  | Meter | 160