Performance Ratio (PR) Calculation for Rooftop and Ground Mount Solar Power Plant

# 1. Introduction

Performance Ratio (PR) is a key indicator of the efficiency and quality of a solar power plant. It represents the ratio of actual energy output to the theoretical energy output under standard test conditions (STC). A higher PR value indicates better system performance.

# 2. Performance Ratio (PR) Formula

The Performance Ratio is calculated using the formula:

PR=EAC kWh X 1000Average IR on tilted panelsWm2X Working Hours Hrs. X AT m2X η .×100

Where:

- PR = Performance Ratio (as a percentage)

- EAC = Actual AC energy output (kWh)

- IR = Irradiance taken from Irradiation sensor (W/m2)

# 3. Calculation Parameters

| Parameter | Description | Formula/Value |
| --- | --- | --- |
| EAC | Measured energy output at inverter AC side | As per inverter data |
| IR | Irradiance taken by sensor for defined time | As per sensor reading |
| Hrs. | Time in which reading is taken (Hours) | Total interval of time |
| AT | Total Solar panel area (m2) | ∑Amodule×Nmodules |
| ηmodule | Module efficiency | Manufacturer’s datasheet |

# 4. Loss Factors Affecting PR

Several loss factors impact the PR value:

| Loss Factor | Description |
| --- | --- |
| Soiling Losses | Dirt accumulation on panels reduces efficiency |
| Temperature Losses | Increased temperature lowers module efficiency |
| Shading Losses | Obstructions cause reduction in generation |
| Inverter Losses | Conversion losses from DC to AC |
| Cable Losses | Transmission losses due to wiring resistance |
| Mismatch Losses | Variations in module characteristics |

# 5. Interpretation

- A PR of 80-90% is excellent.

- A PR of 70-80% is good.

- A PR below 60% may indicate inefficiencies that need addressing.

# 6. Conclusion

Performance Ratio is a crucial metric for assessing the effectiveness of a solar power plant. Regular monitoring and mitigation of losses can improve PR, ensuring optimal energy generation.