# Solar Panel Sizing Calculation (Based on Energy Demand)

## 1. Introduction

Proper solar panel sizing ensures that the photovoltaic (PV) system meets the required energy demand efficiently. This calculation sheet helps determine the number of solar panels needed based on energy consumption, solar irradiance, and system losses.

## 2. Input Parameters

| Parameter | Symbol | Unit | Value |
| --- | --- | --- | --- |
| Daily Energy Consumption | E_d | kWh/day |  |
| Peak Sun Hours | PSH | hours/day |  |
| Solar Panel Efficiency | η_panel | % |  |
| System Efficiency (Including Losses) | η_sys | % |  |
| Rated Power of One Panel | P_panel | Wp |  |

## 3. Formulas for Solar Panel Sizing

### 3.1 Total Energy Required from Solar Panels

Esolar=Edηsys Where:

- Esolar = Total energy required from solar panels (kWh/day)

- Ed = Daily energy consumption (kWh/day)

- ηsys = System efficiency (decimal value)

### 3.2 Required Solar Array Size

Parray=EsolarPSH Where:

- Parray = Required solar array size (kW)

- PSH = Peak sun hours (hours/day)

### 3.3 Number of Solar Panels Required

Npanels=Parray×1000Ppanel Where:

- Npanels = Total number of solar panels required

- Ppanel = Rated power of one panel (Wp)

## 4. Example Calculation

Assuming:

- Ed=30 kWh/day

- PSH=5 hours/day

- ηsys=0.85 (85%)

- Ppanel=400 Wp

### Step 1: Calculate Total Energy Required from Solar Panels

Esolar=300.85=35.29kWh/day

### Step 2: Calculate Required Solar Array Size

Parray=35.295=7.06kW

### Step 3: Calculate Number of Solar Panels Required

Npanels=7.06×1000400=17.65≈18 panels

## 5. Summary Table

| Parameter | Value |
| --- | --- |
| Total Energy Required from Solar Panels | 35.29 kWh/day |
| Required Solar Array Size | 7.06 kW |
| Number of Solar Panels | 18 panels |

## 6. Conclusion

Based on the energy demand of 30 kWh/day, with 5 peak sun hours and 85% system efficiency, a total of 18 solar panels of 400 Wp each are required to meet the demand. This calculation helps in system planning and procurement.