# Depth of Discharge (DoD) & State of Charge (SoC) Calculation for Battery-Connected Solar Power Systems

## 1. Introduction

Battery storage plays a crucial role in solar power systems, ensuring energy availability during non-sunlight hours. Two key parameters in battery performance are Depth of Discharge (DoD) and State of Charge (SoC). Proper calculation of these parameters helps in optimizing battery life, efficiency, and overall system performance.

## 2. Depth of Discharge (DoD) Calculation

### 2.1 Definition

Depth of Discharge (DoD) refers to the percentage of battery capacity that has been used relative to its total capacity. A higher DoD means more battery usage, which can impact battery lifespan.

### 2.2 Formula for DoD

DoD%=Energy Discharged (Wh)Battery Rated Capacity (Wh)×100

### 2.3 Example Calculation

- Battery Capacity: 10 kWh

- Energy Used: 6 kWh DoD=610×100=60%

### 2.4 Recommended DoD Limits

- Lead-Acid Batteries: 50% maximum DoD to prolong life

- Lithium-Ion Batteries: 80-90% DoD is common

- Flow Batteries: Can handle 100% DoD

## 3. State of Charge (SoC) Calculation

### 3.1 Definition

State of Charge (SoC) represents the remaining battery charge as a percentage of the total capacity. It is the inverse of DoD.

### 3.2 Formula for SoC

SoC%=100-DoD%

### 3.3 Example Calculation

Using the previous DoD example: SoC=100-60=40%

### 3.4 Methods for Measuring SoC

- Voltage-Based Estimation (Common for Lead-Acid & Li-ion Batteries)

- Coulomb Counting Method (Precise but requires current sensors)

- Open Circuit Voltage (OCV) Testing

- Battery Management System (BMS) Integration

## 4. Factors Affecting DoD & SoC Accuracy

- Battery Age & Health

- Temperature Variations

- Load Characteristics

- Charge/Discharge Rate (C-rate)

- Self-Discharge of Battery

## 5. Battery Sizing Considerations Based on DoD

To extend battery life, proper sizing must be done based on realistic DoD limits. The required battery capacity can be determined as: Battery Capacity Required (Wh)=Daily Load (Wh)Usable DoD (%)

### Example:

- Daily Load = 5000 Wh

- Usable DoD = 80% for Lithium-Ion Battery Battery Capacity=50000.8=6250 Wh

## 6. Standards & Guidelines

- IEC 61427: Performance testing of batteries for renewable energy systems

- IEEE 485: Battery sizing for stationary applications

- UL 1973: Standard for battery safety

- NEC 690.7: Solar PV and battery system voltage regulations

## 7. Conclusion

By effectively managing Depth of Discharge (DoD) and State of Charge (SoC), solar power system efficiency and battery lifespan can be significantly improved. Proper battery sizing, adherence to industry standards, and monitoring tools are essential for optimal performance.