Solar Hybrid Inverter Sizing Calculation

# 1. Introduction

A solar hybrid inverter is a critical component in solar power systems that integrates both solar PV and battery storage to supply uninterrupted power. Proper sizing of a hybrid inverter ensures system efficiency, reliability, and compatibility with solar panels and batteries.

# 2. Factors Affecting Hybrid Inverter Sizing

- Solar PV Capacity (kWp)

- Battery Storage Capacity (kWh)

- Load Demand (kW)

- Grid and Off-grid Operation Requirements

- Surge Load Handling Capacity

# 3. Formulas for Solar Hybrid Inverter Sizing

### (A) Inverter Sizing Based on Solar PV Capacity

Pinv=PPV×SF

Where:

- Pinv = Required inverter capacity (kW)

- PPV = Total Solar PV Array Power (kWp)

- SF = Safety factor (typically 1.15 to 1.25 to account for efficiency losses)

### (B) Inverter Sizing Based on Load Demand

Pinv=Pload×DF

Where:

- Pload = Maximum connected load demand (kW)

- DF = Derating factor (typically 1.2 to 1.5 for inverter overload protection)

### (C) Inverter Sizing Based on Battery Storage Capacity

Pinv=EbatTbackup×ηinv

Where:

- Ebat = Usable Battery Capacity (kWh)

- Tbackup = Required backup time (hours)

- ηinv = Inverter efficiency (typically 90-95%)

# 4. Standard Inverter Sizing Table

| Solar PV Capacity (kWp) | Battery Capacity (kWh) | Required Inverter Size (kW) |
| --- | --- | --- |
| 3 kWp | 5 kWh | 3.5 – 4 kW |
| 5 kWp | 7 kWh | 5.5 – 6 kW |
| 7.5 kWp | 10 kWh | 8 – 9 kW |
| 10 kWp | 15 kWh | 12 – 13 kW |
| 15 kWp | 20 kWh | 18 – 20 kW |

# 5. Safety Considerations & IEC Standards

- IEC 62109-1 & 62109-2: Safety standards for power inverters

- IEC 61727: Inverter requirements for photovoltaic (PV) systems

- IEC 61683: Efficiency measurement of PV inverters

- IEC 60364-7-712: Electrical installation of PV systems

# 6. Example Calculation

## Example 1: Hybrid Inverter Sizing for a 5 kWp System

- Solar PV Capacity (PPV) = 5 kWp

- Battery Storage (Ebat) = 7 kWh

- Load Demand (Pload) = 4 kW

- Safety Factor (SF) = 1.2

- Inverter Efficiency (ηinv) = 92%

Step 1: Inverter Sizing Based on PV

Pinv=5×1.2=6kW

Step 2: Inverter Sizing Based on Battery Backup

Pinv=72×0.92=3.8kW

Step 3: Inverter Sizing Based on Load

Pinv=4×1.2=4.8kW

Final Inverter Selection: 6 kW Hybrid Inverter

# 7. Conclusion

The hybrid inverter sizing depends on multiple parameters including solar PV capacity, battery backup, and load demand. A proper safety margin should be considered while selecting the inverter to ensure optimal performance and longevity of the system.