AC Cable Sizing Calculation for Solar Power Plants

# 1. Introduction

Proper AC cable sizing is crucial in solar power plant installations to ensure minimal voltage drop, efficiency, and safety. This document provides detailed calculations, electrical formulas, and tables for AC cable selection considering voltage drop, power factor, and conductor type.

# 2. Key Parameters for AC Cable Sizing

- Load Power (P) [kW]

- Operating Voltage (V) [V]

- Current (I) [A]

- Power Factor (PF) [cos(ϕ)]

- Phase Type (Single-phase or Three-phase)

- Cable Length (L) [m]

- Resistivity (ρ) of Conductor [Ω-mm²/m]

- Voltage Drop Limit (%)

# 3. AC Voltage Drop Calculation

### For Single-Phase System:

Vdrop=2×I×L×Rcosϕ+Xsinϕ1000

### For Three-Phase System:

Vdrop=3×I×L×Rcosϕ+Xsinϕ1000

Where:

- R = Resistance of the cable (Ω/km)

- X = Reactance of the cable (Ω/km)

- L = Cable length (m)

- cos(ϕ) = Power factor

- sin(ϕ) = Reactive component

### Allowable Voltage Drop Calculation:

Vmax=Voltage×VoltageDropLimit100

If V_drop ≤ V_max, the cable size is acceptable.

# 4. Current Carrying Capacity Calculation

I=P3×V×cosϕ (For Three-Phase) I=PV×cosϕ (For Single-Phase)

# 5. Cable Selection Based on Conductor Type

| Cable Type | Material | Max. Current Capacity (A) | Resistance (Ω/km) | Reactance (Ω/km) |
| --- | --- | --- | --- | --- |
| Single-Core | Copper | 100 | 0.017 | 0.08 |
| Multi-Core | Copper | 85 | 0.020 | 0.09 |
| Single-Core | Aluminum | 80 | 0.028 | 0.10 |
| Multi-Core | Aluminum | 70 | 0.032 | 0.12 |

# 6. Example Calculation

Given Data:

- Load Power = 50 kW

- Operating Voltage = 415 V

- Power Factor = 0.95

- Cable Length = 100 m

- Allowable Voltage Drop = 3%

Step 1: Calculate Current I=50,0003×415×0.95=73.15A

Step 2: Calculate Allowable Voltage Drop Vmax=415×3100=12.45V

Step 3: Select Cable Type For single-core copper cable: Vdrop=3×73.15×100×0.017×0.95+0.08×0.311000=7.82V

Since 7.82 V ≤ 12.45 V, the cable size is acceptable.

# 7. Conclusion

This document provides a structured approach to AC cable sizing, ensuring efficient and safe solar power plant installations. Selection should always align with local electrical codes and site conditions.