Harmonic Distortion & Power Quality Analysis for Electrical Power Plants

## 1. Introduction

Harmonic distortion is a critical parameter in electrical power systems, affecting efficiency, reliability, and equipment performance. This document provides a detailed calculation sheet for harmonic distortion and power quality analysis, following IEC and IEEE standards.

## 2. Standards & Guidelines

- IEC 61000-3-2: Limits for harmonic current emissions (Equipment input current ≤16 A per phase)

- IEC 61000-3-12: Limits for harmonic current emissions (Equipment input current >16 A per phase)

- IEEE 519-2014: Recommended practices and requirements for harmonic control in electrical power systems

- IEC 60038: Standard voltages

- IEC 62586: Power quality measurement methods

## 3. Harmonic Distortion Parameters

### 3.1 Total Harmonic Distortion (THD)

THD is given by:

THDV=V22+V32+...+Vn2V1×100%

THDI=I22+I32+...+In2I1×100%

Where:

- Vn and In are the voltage and current harmonics at the nth order.

- V1 and I1 are the fundamental voltage and current components.

### 3.2 Individual Harmonic Distortion

IHDn=InI1×100%

Where:

- In = nth harmonic current

- I1 = fundamental current

## 4. Calculation Tables (Without Example)

| Harmonic Order (n) | Voltage Harmonic (Vn) | Current Harmonic (In) | Individual Harmonic Distortion (IHD%) |
| --- | --- | --- | --- |
| 1 (Fundamental) | V1 | I1 | - |
| 2 | V2 | I2 | (I2/I1) * 100% |
| 3 | V3 | I3 | (I3/I1) * 100% |
| ... | ... | ... | ... |
| n | Vn | In | (In/I1) * 100% |

### Total Harmonic Distortion Calculation Table

| Parameter | Value |
| --- | --- |
| THD Voltage (%) | THDV |
| THD Current (%) | THDI |

## 5. Example Calculation (With Example)

Given Data:

- Fundamental Voltage (V1) = 230 V

- Fundamental Current (I1) = 50 A

- Harmonic Current components: I2 = 5A, I3 = 3A, I4 = 2A

### Step 1: Calculate Individual Harmonic Distortion (IHD)

IHD2=550×100=10%

IHD3=350×100=6%

IHD4=250×100=4%

### Step 2: Calculate THD Current

THDI=52+32+2250×100

THDI=25+9+450×100=3850×100≈12.3%

### Example Calculation Table

| Harmonic Order (n) | Current Harmonic (In) | Individual Harmonic Distortion (IHD%) |
| --- | --- | --- |
| 1 (Fundamental) | 50A | - |
| 2 | 5A | 10% |
| 3 | 3A | 6% |
| 4 | 2A | 4% |

### Final Results

| Parameter | Value |
| --- | --- |
| THD Current (%) | 12.3% |

## 6. Conclusion

This report provides a structured approach to harmonic distortion analysis in compliance with IEC and IEEE standards. Power plants should maintain THD below recommended limits to avoid efficiency losses and equipment failures.