Inverter Sizing Calculation (Based on Solar PV Capacity)

# 1. Introduction

Inverter sizing is a critical step in designing a solar power system. The inverter must be appropriately sized to handle the total power generated by the solar PV system and ensure efficient energy conversion. This document provides the calculation methodology for inverter sizing based on solar PV capacity.

# 2. Key Parameters for Inverter Sizing

| Parameter | Symbol | Unit | Description |
| --- | --- | --- | --- |
| Solar PV Capacity | P_PV | kW | Total DC power output of the solar array |
| Inverter Efficiency | ηinv | % | Efficiency of the inverter (typically 95%-98%) |
| Power Factor | PF | - | Typically 0.9 - 1 for grid-tied systems |
| Inverter Rated Capacity | P_inv | kW | Required inverter power rating |
| Maximum DC Voltage | V_dc_max | V | Maximum allowable input voltage for the inverter |
| Maximum AC Output Current | I_ac_max | A | Maximum output current of the inverter |

# 3. Inverter Sizing Calculation

### 3.1 Basic Formula for Inverter Sizing

Pinv=PPV×PFηinv

Where:

- Pinv = Required inverter power rating (kW)

- PPV = Total DC power from the PV system (kW)

- ηinv = Inverter efficiency (in decimal form, e.g., 0.98 for 98%)

- PF = Power factor of the inverter

Example Calculation: If a solar PV system has a capacity of 10 kW, an inverter efficiency of 96% (0.96), and a power factor of 0.95:

Pinv=10×0.950.96=9.89 kW

Thus, a 10 kW inverter would be suitable for this system.

### 3.2 Inverter Oversizing Consideration

Sometimes, oversizing the inverter is recommended to optimize energy yield. The oversizing factor (OF) can be defined as:

OF=PPVPinv

Typical oversizing ratios range between 1.1 and 1.3 to maximize performance.

### 3.3 Inverter Selection Based on Voltage & Current Ratings

To ensure compatibility with the PV array, check:

- Maximum DC Input Voltage (V_dc_max): Ensure that the open-circuit voltage (Voc) of the array does not exceed the inverter’s input limit.

- Maximum DC Input Current (I_dc_max): Ensure the short-circuit current (Isc) of the array does not exceed the inverter’s input current rating.

- AC Output Compatibility: Verify the inverter output matches the grid voltage and frequency.

# 4. Inverter Sizing Table for Different PV Capacities

| PV Capacity (kW) | Power Factor | Efficiency (%) | Required Inverter Size (kW) |
| --- | --- | --- | --- |
| 5 | 0.95 | 96 | 4.95 |
| 10 | 0.95 | 96 | 9.89 |
| 15 | 0.95 | 96 | 14.84 |
| 20 | 0.95 | 96 | 19.79 |

# 5. Conclusion

Proper inverter sizing is essential for the efficient operation of a solar PV system. It must be carefully selected based on the PV array size, efficiency, and grid compatibility. Oversizing may improve performance but should be within allowable limits. Verification of voltage and current ratings ensures safety and operational stability.