Transformer Sizing Calculation for Large-Scale Solar Farms

# 1. Introduction

Transformer sizing is a critical step in the design of large-scale solar farms to ensure efficient energy transfer from inverters to the grid. This document provides a structured approach to calculating transformer capacity based on system parameters.

# 2. Key Parameters for Transformer Sizing

| Parameter | Symbol | Unit | Description |
| --- | --- | --- | --- |
| Total Solar PV Capacity | P_pv | MW | Total installed solar capacity |
| Inverter Efficiency | η_inv | % | Efficiency of the inverter |
| Power Factor | PF | - | Power factor of the system |
| Transformer Efficiency | η_tx | % | Efficiency of the transformer |
| Voltage Level (Primary) | V_p | V | Voltage on the primary side |
| Voltage Level (Secondary) | V_s | V | Voltage on the secondary side |
| Apparent Power | S | MVA | Apparent power of the transformer |

# 3. Calculation Formulas

### 3.1. Apparent Power (S) Calculation

Apparent power in MVA is calculated as:

S=Ppvηinv×PF×ηtx

Where:

- Ppv = Total Solar PV Capacity (MW)

- ηinv = Inverter efficiency

- PF = Power Factor

- ηtx = Transformer Efficiency

### 3.2. Transformer Current Calculation

#### Primary Side Current (I_p)

Ip=S×1063×Vp

#### Secondary Side Current (I_s)

Is=S×1063×Vs

Where:

- Vp = Primary voltage (V)

- Vs = Secondary voltage (V)

- Ip = Primary side current (A)

- Is = Secondary side current (A)

### 3.3. Transformer Rating Selection

The transformer rating should be selected based on the calculated S value, considering a safety margin of 10-20%:

Srated=S×1.2

# 4. Example Calculation

| Parameter | Value |
| --- | --- |
| Total Solar PV Capacity (P_pv) | 50 MW |
| Inverter Efficiency (η_inv) | 98% |
| Power Factor (PF) | 0.9 |
| Transformer Efficiency (η_tx) | 99% |
| Primary Voltage (V_p) | 33 kV |
| Secondary Voltage (V_s) | 400 V |

#### Step 1: Calculate Apparent Power (S)

S=500.98×0.9×0.99=56.84MVA

#### Step 2: Calculate Primary & Secondary Current

Ip=56.84×1063×33000=994A

Is=56.84×1063×400=82,079A

#### Step 3: Transformer Rating Selection

Srated=56.84×1.2=68.2MVA

The selected transformer should be rated 70 MVA to accommodate safety margins.

# 5. Conclusion

Transformer sizing is essential for ensuring stable and efficient energy distribution in large-scale solar farms. This document provides a step-by-step approach to determining the appropriate transformer rating based on system parameters and industry best practices.