DC Cable Sizing Calculation (Voltage Drop, Ampacity)

# 1. Introduction

Proper DC cable sizing is essential in solar power plants to minimize voltage drop, ensure electrical efficiency, and prevent overheating. This document outlines the key formulas and steps for determining the correct cable size based on voltage drop and ampacity.

# 2. Parameters Required

| Parameter | Symbol | Unit | Description |
| --- | --- | --- | --- |
| Current | I | A (Amperes) | Load current flowing through the cable |
| Voltage | V | V (Volts) | System voltage |
| Resistance per unit length | R | Ω/m | Resistance of the conductor per meter |
| Conductor Length | L | m | Total length of the conductor |
| Voltage Drop | VD | V | Allowable voltage drop |
| Cable Cross-Sectional Area | A | mm² | Size of the cable |
| Allowable Ampacity | I_max | A | Maximum current capacity of the cable |

# 3. Voltage Drop Calculation

The voltage drop (VD) in a DC circuit is calculated using: VD=2×I×R×L where:

- I = Current (A)

- R = Resistance of cable (Ω/m)

- L = One-way length of the cable (m)

- 2 = Accounts for both positive and negative conductors

Percentage Voltage Drop Calculation: %VD=VDV×100

Acceptable Limits:

- For solar PV DC circuits, the voltage drop should be ≤ 2% for efficiency.

# 4. Cable Ampacity Calculation

The current carrying capacity (ampacity) of the cable is determined by: I≤Imax where:

- I = Load current (A)

- I_max = Maximum allowable ampacity of the selected cable (A)

Ampacity depends on:

- Cable material (Copper/Aluminum)

- Insulation type (PVC, XLPE, etc.)

- Installation conditions (Ambient temperature, Conduit, etc.)

Ampacity values are generally obtained from standard tables (e.g., NEC, IEC, IS).

# 5. Cable Selection Process

- Calculate Voltage Drop: Ensure it is within acceptable limits.

- Check Ampacity: Ensure the selected cable can handle the load current.

- Consider Environmental Factors: Such as derating due to temperature and installation conditions.

- Confirm Standard Compliance: Use IS/IEC/NEC standards for cable selection.

# 6. Example Calculation

### Given Data:

- System Voltage (V) = 1000V

- Load Current (I) = 50A

- Cable Resistance (R) = 0.00041 Ω/m (for 25 mm² Cu)

- Length of Cable (L) = 50m (one way)

### Step 1: Voltage Drop Calculation

VD=2×50×0.00041×50 VD=2.05V

### Step 2: Percentage Voltage Drop

%VD=2.051000×100 %VD=0.205% (within limits)

### Step 3: Ampacity Check

For a 25 mm² Cu conductor, max ampacity = 135A (as per NEC/IEC tables). Since I (50A) < I_max (135A), the cable is suitable.

# 7. Conclusion

Proper cable sizing ensures efficiency and safety in DC systems. This document provides a structured approach to determining cable size based on voltage drop and ampacity. Always verify selections against applicable electrical codes (NEC, IEC, IS) and site-specific conditions.