Earthing & Grounding Resistance Calculation

# 1. Introduction

Earthing and grounding are essential for electrical safety in solar power plants. Proper grounding ensures the safe dissipation of fault currents, protects equipment, and enhances overall system reliability. This document provides detailed calculations for earthing resistance.

# 2. Parameters Required for Earthing Resistance Calculation

| Parameter | Symbol | Unit | Description |
| --- | --- | --- | --- |
| Resistivity of Soil | ρ | Ω.m | Soil resistivity varies with location |
| Depth of Electrode | h | m | Depth at which electrode is buried |
| Diameter of Electrode | d | m | Diameter of the grounding rod |
| Length of Electrode | L | m | Length of the grounding rod |
| Number of Electrodes | N | - | Number of grounding electrodes in parallel |

# 3. Mathematical Formulas

## 3.1 Resistance of a Single Rod Electrode

The resistance of a vertical grounding rod is given by:

R=ρ2πLln4Ld

Where:

- R = Grounding resistance (Ohms)

- ρ = Soil resistivity (Ohm-meter)

- L = Length of the electrode (meters)

- d = Diameter of the electrode (meters)

## 3.2 Resistance of Multiple Rod Electrodes

For N electrodes in parallel, the total resistance Rt is given by:

Rt=RN

Where:

- R = Resistance of a single electrode

- N = Number of electrodes

# 4. Sample Calculation

Given Data:

- Soil resistivity, ρ=100Ω.m

- Length of electrode, L=2.5m

- Diameter of electrode, d=0.05m

- Number of electrodes, N=4

Step 1: Calculate Resistance of Single Electrode

R=1002π×2.5ln4×2.50.05

R=10015.7ln100.05

R=10015.7ln200

R=10015.7×5.3

R≈33.8Ω

Step 2: Calculate Total Resistance for 4 Electrodes in Parallel

Rt=33.84=8.45Ω

# 5. Compliance Standards

- IS 3043: Code of practice for earthing

- IEEE 80: Guide for safety in AC substation grounding

- IEC 60364-5-54: Electrical installations of buildings – Earthing arrangements

# 6. Conclusion

Proper earthing is crucial for the safe operation of a solar power plant. The calculated resistance should meet local electrical safety standards to ensure protection against electrical faults.