Fuse & DC Circuit Breaker Sizing Calculation

# 1. Introduction

Proper sizing of fuses and DC circuit breakers is crucial to protect the solar power system from overcurrent conditions, short circuits, and potential fire hazards. This document provides step-by-step calculations, electrical formulas, and reference tables for selecting appropriate fuse and DC circuit breaker ratings.

# 2. Key Electrical Parameters

- Voltage (V): System operating voltage (Vdc)

- Current (I): Maximum expected current (A)

- Short-Circuit Current (Isc): Maximum current a solar panel or string can generate under fault conditions (A)

- Safety Factor (SF): Typically 1.25 (25% margin as per NEC standards)

# 3. Fuse Sizing Calculation

## Formula:

Ifuse=Imax×SF

Where:

- Ifuse = Fuse rating (A)

- Imax = Maximum circuit current (A)

- SF = Safety factor (typically 1.25)

### Example Calculation:

- Given: Imax=10A, SF = 1.25

- Ifuse=10×1.25=12.5A

- Standard fuse rating: 15A (rounded up to the nearest available rating)

### Recommended Fuse Types:

- MC4 inline fuse (for PV modules)

- NH fuses (for DC combiner boxes)

- DC cartridge fuses (for inverters and battery protection)

# 4. DC Circuit Breaker Sizing Calculation

## Formula:

Ibreaker=Inom×SF

Where:

- Ibreaker = Circuit breaker rating (A)

- Inom = Nominal system current (A)

- SF = Safety factor (typically 1.25 - 1.5 depending on application)

### Example Calculation:

- Given: Inom=20A, SF = 1.25

- Ibreaker=20×1.25=25A

- Standard breaker rating: 25A or 32A (rounded up)

### Recommended DC Circuit Breaker Types:

- DIN Rail-mounted DC breakers (for combiner boxes and inverter inputs)

- MCCB (Molded Case Circuit Breakers) (for large-scale solar plants)

- Battery DC breakers (for hybrid and storage systems)

# 5. Reference Table for Fuse & Circuit Breaker Selection

| System Voltage (V) | Max Current (A) | Recommended Fuse (A) | Recommended Breaker (A) |
| --- | --- | --- | --- |
| 12V DC | 10A | 15A | 20A |
| 24V DC | 20A | 25A | 32A |
| 48V DC | 30A | 40A | 50A |
| 110V DC | 50A | 63A | 80A |
| 150V DC | 75A | 100A | 125A |
| 600V DC | 100A | 125A | 150A |

# 6. Compliance & Standards

- NEC 690.9 (Overcurrent Protection)

- IEC 60269 (Low-voltage fuse standard)

- UL 248 (Fuses for solar applications)

- IEC 60947-2 (DC Circuit Breakers)

# 7. Conclusion

This document provides a structured approach to selecting appropriate fuse and DC circuit breaker ratings based on current, safety factors, and industry standards. Proper selection ensures system safety, longevity, and compliance with international electrical codes.