Inverter MPPT Voltage & Current Compatibility Check

# 1. Introduction

Ensuring the compatibility of the solar module string voltage and current with the Maximum Power Point Tracking (MPPT) range of the inverter is crucial for optimal system performance. This calculation sheet provides the formulas and methodology for verifying this compatibility.

# 2. Input Parameters

| Parameter | Symbol | Value | Unit |
| --- | --- | --- | --- |
| Open Circuit Voltage (per module) | Voc |  | V |
| Maximum Power Voltage (per module) | Vmp |  | V |
| Short Circuit Current (per module) | Isc |  | A |
| Maximum Power Current (per module) | Imp |  | A |
| Temperature Coefficient of Voc | Tcv |  | %/°C |
| Minimum Ambient Temperature | T_min |  | °C |
| Maximum Ambient Temperature | T_max |  | °C |
| Number of Modules in Series | N_series |  | - |
| Number of Strings in Parallel | N_parallel |  | - |
| Inverter MPPT Voltage Range (Min-Max) | V_MPPT (min-max) |  | V |
| Inverter MPPT Maximum Current | I_MPPT max |  | A |

# 3. Voltage Compatibility Check

### Step 1: Calculate the Lowest String Voltage (Cold Conditions)

Formula: Vstringmin=Nseries×Voc×1+Tcv100×Tmin-25

### Step 2: Calculate the Highest String Voltage (Hot Conditions)

Formula: Vstringmax=Nseries×Vmp×1+Tcv100×Tmax-25

### Step 3: Verify Compatibility with Inverter MPPT Range

- Ensure that: VMPPTmin≤Vstringmin≤VMPPTmax VMPPTmin≤Vstringmax≤VMPPTmax

If the calculated values are outside the MPPT range, adjust the number of modules in series (N_series).

# 4. Current Compatibility Check

### Step 1: Calculate the Maximum String Current

Formula: Istringmax=Nparallel×Isc

### Step 2: Verify Compatibility with Inverter MPPT Current Rating

- Ensure that: Istringmax≤IMPPTmax

If the string current exceeds the MPPT current limit, reduce the number of parallel strings (N_parallel).

# 5. Conclusion

By ensuring that both voltage and current values fall within the inverter’s MPPT range, we optimize system efficiency and prevent potential damage to the inverter. This compatibility check is a vital step in solar PV system design.