Solar Module String Sizing Calculation (Voc, Isc, Vmp, Imp)

# 1. Introduction

Solar module string sizing is a crucial step in designing a photovoltaic (PV) system. It ensures that the modules are connected in an optimal configuration to match the inverter’s operating voltage and current ranges. This document outlines the calculation process for determining the appropriate number of modules per string based on electrical parameters such as Open Circuit Voltage (Voc), Short Circuit Current (Isc), Maximum Power Voltage (Vmp), and Maximum Power Current (Imp).

# 2. Key Electrical Parameters

| Parameter | Symbol | Definition |
| --- | --- | --- |
| Open Circuit Voltage | Voc | The maximum voltage of a solar module when no load is connected. |
| Short Circuit Current | Isc | The maximum current of a solar module when the terminals are shorted. |
| Maximum Power Voltage | Vmp | The voltage at which the module delivers maximum power. |
| Maximum Power Current | Imp | The current at which the module delivers maximum power. |
| Temperature Coefficient of Voltage | TC_Voc | Percentage decrease in voltage per °C rise in temperature. |
| Temperature Coefficient of Current | TC_Isc | Percentage increase in current per °C rise in temperature. |

# 3. Calculation Formulas

## 3.1 Determining Maximum & Minimum Voc for Sizing

### 3.1.1 Maximum Voc (Cold Temperature Condition)

Vocmax=Vocstc×1+TCVoc×Tmin-Tstc

Where:

- Vocstc = Voc at standard test conditions (STC, 25°C, 1000W/m²)

- TCVoc = Temperature coefficient of Voc (%/°C)

- Tmin = Minimum ambient temperature (°C)

- Tstc = Standard test condition temperature (25°C)

### 3.1.2 Minimum Voc (Hot Temperature Condition)

Vocmin=Vocstc×1+TCVoc×Tmax-Tstc

Where:

- Tmax = Maximum ambient temperature (°C)

## 3.2 String Sizing for Inverter Compatibility

### 3.2.1 Maximum Number of Modules in a String

Nmax=VinvertermaxVocmin

Where:

- Vinvertermax = Maximum DC input voltage of the inverter

### 3.2.2 Minimum Number of Modules in a String

Nmin=VinverterminVocmax

Where:

- Vinvertermin = Minimum DC input voltage of the inverter

## 3.3 String Current Considerations

### 3.3.1 Maximum String Current

Istring=Imp×Nparallel

Where:

- Nparallel = Number of parallel strings

Ensure that:

Istring≤Iinvertermax

Where:

- Iinvertermax = Maximum DC input current of the inverter

# 4. Example Calculation

## Given Data:

- Solar Module Voc = 45.2V

- Isc = 10.2A

- Vmp = 38.1V

- Imp = 9.8A

- TC_Voc = -0.3%/°C

- Minimum Temperature = -10°C

- Maximum Temperature = 50°C

- Inverter Voltage Range = 200V – 600V

### Step 1: Calculate Voc_max and Voc_min

Vocmax=45.2×[1+-0.003×-10-25]=49.2V

Vocmin=45.2×[1+-0.003×50-25]=41.7V

### Step 2: Calculate Number of Modules per String

Nmax=60049.2=12.2≈12 (round down)

Nmin=20041.7=4.8≈5 (round up)

Thus, the number of modules per string should be between 5 to 12.

# 5. Conclusion

Proper solar module string sizing ensures that the system operates within the inverter’s voltage and current limits, maximizing efficiency and longevity. Using the above calculations, the optimal number of modules per string can be determined to ensure safe and efficient operation.