# Ballast Weight Calculation for Non-Penetrative Mounting of Solar Module Structure

## 1. Introduction

Ballast weight is used in non-penetrative solar mounting systems to counteract forces such as wind and prevent system displacement. Proper ballast calculation ensures structural stability while avoiding unnecessary weight that may stress the rooftop or ground surface.

## 2. Governing Standards

The ballast weight calculation follows guidelines from:

- IS 875 (Part-3) - Wind Loads

- ASCE 7-16 - Minimum Design Loads

- IEC 62548 - PV Array Design Requirements

- UL 2703 - PV Mounting System Safety

## 3. Calculation Parameters

| Parameter | Symbol | Unit | Description |
| --- | --- | --- | --- |
| Wind Speed | V | m/s | Design wind speed as per IS 875 Part-3 |
| Roof Height | h | m | Height of the installation above ground |
| Roof Exposure Factor | Kz | - | Factor based on surroundings |
| Module Area | A | m² | Area of a single module |
| Number of Modules | N | - | Total modules in the system |
| Drag Coefficient | Cd | - | Aerodynamic coefficient (typically 1.2 - 2.0) |
| Safety Factor | SF | - | Applied margin of safety |
| Gravity Acceleration | g | m/s² | 9.81 m/s² |
| Ballast Weight per Unit | Wb | kg | Weight required per unit |

## 4. Ballast Weight Calculation Formulas

### 4.1 Wind Load Calculation

The wind load on the module structure is determined using: Fw=0.613×Kz×V2×Cd×A Where:

- F_w = Wind force per module (N)

- 0.613 = Air density constant

- Kz = Roof exposure factor

- V = Wind speed (m/s)

- Cd = Drag coefficient

- A = Module area (m²)

### 4.2 Required Ballast Weight

The ballast weight is calculated to counteract the uplift force caused by wind: Wb=Fw×SFg Where:

- Wb = Required ballast weight (kg)

- F_w = Wind force per module (N)

- SF = Safety factor

- g = Gravitational acceleration (9.81 m/s²)

## 5. Example Calculation

### Given Data:

| Parameter | Value |
| --- | --- |
| Wind Speed (V) | 40 m/s |
| Roof Height (h) | 10 m |
| Roof Exposure Factor (Kz) | 1.0 |
| Module Area (A) | 2 m² |
| Drag Coefficient (Cd) | 1.5 |
| Safety Factor (SF) | 1.5 |

### Step-by-Step Calculation:

- Wind Load Calculation: Fw=0.613×1.0×402×1.5×2 Fw=0.613×1.0×1600×1.5×2 Fw=2943.36N

- Ballast Weight Calculation: Wb=2943.36×1.59.81 Wb=4415.049.81 Wb=450.19kg (per module)

## 6. Summary & Considerations

- The total ballast weight depends on the number of modules and layout.

- Adjust ballast distribution to ensure uniform load distribution on the roof.

- Consider additional loads such as snow or seismic forces in specific regions.

- Use concrete blocks or other non-penetrative weights for securing structures.